## NXr_866-meas1
IP= | 126.4.100.101 | Email | darryl.brown@emerson.com | SMTP server= | 10.16.67.249 | Enable= | y
PointId | Point Label | LifeId | Life Measures | Data Offset | Resolution | Measure Value | Data Scaling | Optional Delay (sec) | Unit Of Measure | Run y / n
4097 | System Input RMS A-B | 90 | Mains L1-L2 voltage | 0 | 0 | 3000 | 1 | 0 | VAC | y
4099 | System Input RMS B-C | 91 | Mains L2-L3 voltage | 0 | 0 | 4000 | 1 | 0 | VAC | y
4101 | System Input RMS C-A | 92 | Mains L3-L1 voltage | 0 | 0 | 5000 | 1 | 0 | VAC | y
4113 | System Input RMS Current Phase A | 125 | Mains Current Ph1 | 0 | 0 | 100 | 1 | 0 | A AC | y
4114 | System Input RMS Current Phase B | 126 | Mains Current Ph2 | 0 | 0 | 200 | 1 | 0 | A AC | y
4115 | System Input RMS Current Phase C | 127 | Mains Current Ph3 | 0 | 0 | 300 | 1 | 0 | A AC | y
4105 | System Input Frequency | 36 | Mains Frequency | 0 | 1 | 599 | 1 | 0 | Hz | y
4096 | System Input RMS A-N | 87 | Mains L1-N voltage | 0 | 0 | 2500 | 1 | 0 | VAC | y
4098 | System Input RMS B-N | 88 | Mains L2-N voltage | 0 | 0 | 3500 | 1 | 0 | VAC | y
4100 | System Input RMS C-N | 89 | Mains L3-N voltage | 0 | 0 | 4500 | 1 | 0 | VAC | y
4116 | System Input Power Factor Phs A | 164 | Input power factor L1 | 0 | 2 | 7000 | 1 | 0 |  | y
4117 | System Input Power Factor Phs B | 165 | Input power factor L2 | 0 | 2 | 8000 | 1 | 0 |  | y
4118 | System Input Power Factor Phs C | 166 | Input power factor L3 | 0 | 2 | 9000 | 1 | 0 |  | y
4128 | Bypass Input Voltage RMS A-N | 9 | Reserve Voltage Ph1 | 0 | 0 | 1500 | 1 | 0 | VAC | y
4129 | Bypass Input Voltage RMS B-N | 10 | Reserve Voltage Ph2 | 0 | 0 | 1750 | 1 | 0 | VAC | y
4130 | Bypass Input Voltage RMS C-N | 11 | Reserve Voltage Ph3 | 0 | 0 | 2000 | 1 | 0 | VAC | y
4131 | Bypass Input Frequency | 12 | Reserve Frequency | 0 | 1 | 699 | 1 | 0 | Hz | y
4150 | Battery Time Remaining | 163 | Battery time remaining | 0 | 0 | 1000000 | 1 | 0 | min | y
4155 | Battery Volts for Cabinet | 7 | Battery Voltage | 0 | 0 | 480 | 1 | 0 | VDC | y
4156 | Battery Temperature for Cabinet | 32 | Battery temperature | 0 | 0 | 100 | 1 | 0 | deg C | y
4291 | Inlet Air Temperature | 33 | Inlet Air temperature | 0 | 0 | 200 | 1 | 0 | deg C | y
4149 | DC Bus Current | 4 | Dc Current | 0 | 0 | 1000 | 1 | 0 | A DC | y
4385 | System Output Voltage RMS A-N | 20 | Output Voltage Ph1 | 0 | 0 | 5500 | 1 | 0 | VAC | y
4386 | System Output Voltage RMS B-N | 21 | Output Voltage Ph2 | 0 | 0 | 6500 | 1 | 0 | VAC | y
4387 | System Output Voltage RMS C-N | 22 | Output Voltage Ph3 | 0 | 0 | 7500 | 1 | 0 | VAC | y
4204 | System Output RMS Current Phs A | 25 | Load Current Ph1 | 0 | 0 | 20 | 1 | 0 | A AC | y
4205 | System Output RMS Current Phs B | 26 | Load Current Ph2 | 0 | 0 | 30 | 1 | 0 | A AC | y
4206 | System Output RMS Current Phs C | 27 | Load Current Ph3 | 0 | 0 | 40 | 1 | 0 | A AC | y
4207 | System Output Frequency | 23 | Output Frequency | 0 | 1 | 799 | 1 | 0 | Hz | y
4201 | System Output Voltage RMS A-B | 198 | System Output Voltage RMS A-B | 0 | 0 | 1000 | 1 | 0 | VAC | y
4202 | System Output Voltage RMS B-C | 199 | System Output Voltage RMS B-C | 0 | 0 | 2000 | 1 | 0 | VAC | y
4203 | System Output Voltage RMS C-A | 200 | System Output Voltage RMS C-A | 0 | 0 | 3000 | 1 | 0 | VAC | y
4210 | System Output Power Factor Phs A | 122 | Power Factor Ph1 | 0 | 2 | 5000 | 1 | 0 |  | y
4211 | System Output Power Factor Phs B | 123 | Power Factor Ph2 | 0 | 2 | 6000 | 1 | 0 |  | y
4212 | System Output Power Factor Phs C | 124 | Power Factor Ph3 | 0 | 2 | 7000 | 1 | 0 |  | y
4223 | System Output Pct Power Phase A | 201 | System Output Pct Power Phase A | 0 | 0 | 100000 | 1 | 0 | % | y
4224 | System Output Pct Power Phase B | 202 | System Output Pct Power Phase B | 0 | 0 | 200000 | 1 | 0 | % | y
4225 | System Output Pct Power Phase C | 203 | System Output Pct Power Phase C | 0 | 0 | 300000 | 1 | 0 | % | y
4209 | System Output Apparent Power | 111 | Load apparent power | 0 | 0 | 400000 | 1 | 0 | kVA | y
4208 | System Output Power | 112 | Load real power | 0 | 0 | 500000 | 1 | 0 | kW | y
5159 | Output Current Crest Factor Phs A | 167 | Output current crest factor L1 | 0 | 1 | 10 | 1 | 0 |  | y
5160 | Output Current Crest Factor Phs B | 168 | Output current crest factor L2 | 0 | 1 | 20 | 1 | 0 |  | y
5161 | Output Current Crest Factor Phs C | 169 | Output current crest factor L3 | 0 | 1 | 30 | 1 | 0 |  | y