## Sheet1
IP= | 126.4.100.101 | Email | darryl.brown@emerson.com | SMTP server= | 10.16.67.249 | Enable= | y
PointId | Point Label | LifeId | life event | ORed event | EmerDelay | Event State | multi-module index | Optional Delay (sec) | EmerDelay y / n | Run y / n
4122 | System Input Power Problem | 202 | Primary mains power failure |  | Immediate | 19 | 0 | 0 | y | y
4143 | Bypass Static Switch Unavailable | 579 | Bypass static switch fault / meas. defective |  |  | 19 | 0 | 0 | n | n
4146 | System Input Phs Rotation Error | 204 | Primary mains wrong phase rotation |  | 1 minute | 19 | 0 | 0 | n | y
Note on B1: IP Address for the Velocity Simulator. Use 127.0.0.1 if this script is running on same PC as Simulator. -or- Use address of remote PC where the simulator is running. Ensure that "Remote Control" check box is enabled on the Velocity simulator
Note on C1: Email address
Note on F1: 10.16.67.249 = inetmail.emersn.net
Note on G1: Send email when test is complete if enable = y (Yes)
Note on F2: Delay until 'call' is made to the LIFE Station after Active Event transition. If cell is empty, the event is sent with the next Routine call
Note on G2: Clear = 0 Message = 3 Warn = 11 Alarm = 19 Fault = 27
Note on H2: Commonly indexed points are: Battery Cabinets on UPS systems. Temp semsors of Cooling systems. Where: 0 is the first, 1 is the second, etc.
Note on I2: The delay starts after the Event State transition. This delay is combined with EmerDelay when it is enabled (y).
Note on J2: Use Emergency Delay: y = Yes n = No Emergency Delay is added to the Optional Delay Example 1: EmerDelay = 1 minute Opt Delay = 10 sec Cell in this Column = y Step delay = 70 seconds. Example 2: EmerDelay = 1 minute Opt Delay = 10 sec Cell in this Column = n Step delay = 10 seconds.
Note on K2: Run this step: y = Yes n = No use lower case