## NXl_2199-events
PointId | LifeId | LifeEvents | ORed events | EmerCall | EmerDelay | InReport | Emergency Call Status | Other Call Status | Alarm Condition | PgmName | Point Label | EngReference | EngDescription
| 0 | Events Data lost |  | No |  | No | Normal | Normal | event |  | Data Lost
| 1 | Service active |  | Yes | 18 hours | Yes | Warning | Warning | event |  | Service Active
| 2 | Adjust time |  | No |  | No | Normal | Normal | event |  | Adjust Time
| 990 | Negative Adjust time |  | No |  | No | Normal | Normal | event |  | Negative Adjust Time
| 1659 | UPS board hasn't detected the UPS |  | Yes | 1 hour | No | Severe Warning | Severe Warning | event |  | UPS board hasn't detected the UPS
| 1860 | Changed SN or type |  | Yes | Immediate | No | Alarm | Alarm | event |  | Unity board reports new S/N or type
| 5 | Unit just supplied |  | Yes | Immediate | No | Severe Warning | Warning | event |  | Unit Just Supplied
| 84 | Measures Data lost |  | No |  | No | Normal | Normal | event |  | Measure Data Lost
4122 | 202 | Primary mains power failure |  | Yes | Immediate | Yes | Normal | Normal | event | evt_sys_inpNotQualified | System Input Power Problem | tag=nxlEvents:EventID1 | The input is not qualified to provide power to the system. This may be due to system input over-voltage, system input under-voltage, system input frequency out of range, or other similar issues.This data definition is intended to be used with devices that only have one system input. The system input may be single, 2-phase or 3-phase. A system bypass input is NOT considered to be a second system input. For system bypass input definitions see @todo.Do NOT use this data definition if the device has more that one system input. An example of a device that has more than one system input is the STS2. For devices with multiple system inputs, see the following data definitions: @todo.The system input is defined as the source of power (utility or mains) for the device.
4132 | 594 | Bypass overload operation | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_byp_outOverloadPhsA | Bypass Overload Phase A | tag=nxlEvents:EventID21 | With the load on bypass static switch, the measured phase A output RMS current has exceeded a specified percentage of the nominal per-phase RMS current rating.Event clears when measured phase A output has dropped to a specified percentage of nominal RMS current rating
4133 | 594 | Bypass overload operation | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_byp_outOverloadPhsB | Bypass Overload Phase B | tag=nxlEvents:EventID22 | With the load on bypass static switch, the measured phase B output RMS current has exceeded a specified percentage of the nominal per-phase RMS current rating.Event clears when measured phase B output has dropped to a specified percentage of nominal RMS current rating
4134 | 594 | Bypass overload operation | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_byp_outOverloadPhsC | Bypass Overload Phase C | tag=nxlEvents:EventID23 | With the load on bypass static switch, the measured phase C output RMS current has exceeded a specified percentage of the nominal per-phase RMS current rating.Event clears when measured phase C output has dropped to a specified percentage of nominal RMS current rating
4135 | 593 | Bypass mains power failure |  | Yes | Immediate | Yes | Normal | Normal | event | evt_byp_unavail | Bypass Not Available | tag=nxlEvents:EventID14 | This summary event is asserted when the bypass is not available. Possible reasons for this might include, but is not limited to the following: Bypass Sync Error, Bypass Line Fail, Bypass Overvoltage, Bypass Undervoltage, Bypass Phase Rotation Error, etc.
4138 | 545 | Transfer to bypass inhibited | X | No |  | Yes | Normal | Normal | event | evt_byp_autoReXfrFailed | Bypass Auto Retransfer Failed | tag=nxlEvents:EventID27 | A recoverable transfer from bypass to inverter did not happen within the specified time interval. Further attempts to retransfer to inverter are inhibited.Reference 'evt_byp_autoReXfrPrimed'.
4139 | 545 | Transfer to bypass inhibited | X | No |  | Yes | Normal | Normal | event | evt_byp_excessAutoReXfr | Bypass - Excess Auto Retransfers | tag=nxlEvents:EventID28 | Indicates too many transfers from bypass to inverter have occured in the specified time interval. Automatic retransfer to inverter is inhibited (manual retransfer may still be allowed).
4142 | 650 | Static switch overload warning |  | Yes | 10 minutes | No | Severe Warning | Severe Warning | event | evt_byp_sbsOverload | Bypass Static Switch Overload | tag=nxlEvents:EventID119 | At least one phase of the static bypass switch (SBS) power dissipation limit has been exceeded (RMS current vs time curve). Generally, the UPS willtake action to protect the SBS from the overload condition.
4143 | 579 | Bypass static switch fault / meas. defective |  | No |  | No | Normal | Normal | event | evt_byp_sbsUnavail | Bypass Static Switch Unavailable | tag=nxlEvents:EventID120 | Summary event based on the detection of a SBS failure. Some of the possible causes include, but are not limited to the following: SBS Phase Open , SBS SCR Shorted, Static Bypass Switch Overload Exceeded, Bypass Power Supply Fail, Static Bypass Switch Fuse Failure, etc
4144 | 1861 | Bypass Excessive Pulse Parallel |  | No |  | No | Normal | Normal | event | evt_byp_excessPulseParallel | Bypass Excessive Pulse Parallel | tag=nxlEvents:EventID218 | The system has performed too many pulse parallel operations within the specified time interval. A pulse parallel operation is a momentary operation of the static bypass switch (SBS) in parallel with the inverter.
4145 | 1862 | Bypass Auto Transfer Failed |  | No |  | No | Normal | Normal | event | evt_byp_autoXfrFailed | Bypass Auto Transfer Failed | tag=nxlEvents:EventID124 | An automatic transfer to static bypass failed.
4146 | 204 | Primary mains wrong phase rotation |  | Yes | 1 minute | Yes | Alarm | Warning | event | evt_sys_inpPhsRotation | System Input Phs Rotation Error | tag=nxlEvents:EventID3 | The power conductors on the input line are not wired to the UPS in the sequence preferred for the rectifier (A-B-C).With the input source voltage above minimum threshold, the phase rotation is not A-B-C. It becomes inactive when the phase rotation is A-B-C with source voltage above minimum threshold.
4147 | 423 | Current limit |  | Yes | 1 minute | yes | Normal | Normal | event | evt_sys_inpCurrentLimit | System Input Current Limit | tag=nxlEvents:EventID7 | The RMS input current has reached the input current limit threshold. One or more of the input phases reached the current limit threshold.It becomes inactive when RMS current returns below a specified percentage of the threshold.
4162 | 309 | Battery Shutdown Imminent |  | Yes | 10 minutes | Yes | Severe Warning | Severe Warning | event | evt_bat_low | Battery Low | tag=nxlEvents:EventID31 | The calculated battery time remaining has reached the battery low threshold. This event is NOT active during a battery test or while operating on mains/utility. It becomes inactive when the calculated battery time remaining is above the low battery threshold, or normal operation on utility/mains resumes. This event may or may not remain active past the end-of-discharge.
4164 | 232 | Battery charger failure |  | Yes | 10 minutes | No | Severe Warning | Warning | event | evt_bat_chargeError | Battery Charging Error | tag=nxlEvents:EventID229 | The battery is not charging properly. This could be caused by a number of reasons, including but not limited to: battery charger failure, battery failure, etc. It becomes inactive when battery charging returns to normal.Raptor Specific: Active Condition _ With the battery charging in the Constant Voltage Charging - Lead Acid (143319) mode and after a successful battery self test, if any battery breaker is closed, and the battery charging voltage not reduced and the battery voltage has not reached a specified setting within a specified period of time. Recover Condition _ The battery voltage has reached a specified setting or Input Undervoltage (126819) is active.
4165 | 1863 | Battery Charging Reduced-Extrnl |  | No |  | No | Normal | Normal | event | evt_bat_chargeReducedExt | Battery Charging Reduced-Extrnl | tag=nxlEvents:EventID264 | Using a reduced battery charging algorithm due to an external signal. For example, this might be active when operating on a generator to minimize the generator's load. It becomes inactive when normal battery charging is no longer inhibited by the external signal.Raptor Specific - Condition - If input contact interface 1, Ch2 assignment is 'Pre-assigned', i.e. Reduced Batt ILimit" then see operation for Reduced Battery Charging Current (144495). Recovery - Input contact channel signal is not active or Input Contact Isolation #1 Communication Failure (138958) is active."
4166 | 338 | Battery capacity too small |  | No |  | No | Normal | Normal | event | evt_bat_capacityLow | Battery Capacity Low | tag=nxlEvents:EventID34 | The battery capacity is low. There are various possible reasons for this event, including but not limited to: a battery is offline, the battery age has reduced its capabilities, etc. It becomes inactive when normal battery capacity is restored. For a system configuration without batteries, this event should not be supported.Raptor Specific - Condition for Battery Capacity Low: With the load on UPS inverter and at least one battery breaker is closed, at least one other battery breaker is open. Recover Condition: When all battery breakers are closed or the inverter is off or the system has transferred to bypass
4168 | 308 | Battery discharging |  | No |  | Yes | Normal | Normal | event | evt_bat_discharging | Battery Discharging | tag=nxlEvents:EventID35 | The battery is discharging. This is active when power is being withdrawn from the battery. NOTE: This is not activated due to a battery test.Becomes inactive when the batteries are charging.
4169 | 315 | High battery temperature | X | Yes | 1 minute | Yes | Severe Warning | Severe Warning | event | evt_bat_tempImbalance | Battery Temperature Imbalance | tag=nxlEvents:EventID150 | Any two active battery temperatures have a difference greater than the difference threshold. In this context, the term 'active' means that the battery is configured to be part of the system.Becomes inactive when the battery temperature differences are less than the difference threshold.
4170 | 1841 | Battery Equalize |  | No |  | No | Normal | Normal | event | evt_bat_equalize | Battery Equalize | tag=nxlEvents:EventID132 | The rectifier output voltage is increased to equalize the battery voltage level. It becomes inactive when the equalize algorithm completes OR battery discharge is required.
4173 | 303 | Battery disconnected |  | Yes | 1 minute | Yes | Severe Warning | Severe Warning | event | evt_bat_mainDisconnectOpen | Main Battery Disconnect Open | tag=nxlEvents:EventID179 | Main battery disconnect is open.Becomes inactive when the main battery disconnect is closed.
4174 | 332 | Battery temperature fault |  | No |  | Yes | Severe Warning | Warning | event | evt_bat_tempSnsrFail | Battery Temperature Sensor Fault | tag=nxlEvents:EventID149 | A battery temperature sensor fault has been detected. This is a summary event based on the detection of at least one or more battery temperature sensors faults.Becomes inactive when all temperature sensor fault conditions clear.
4175 | 513 | Reserve mains frequency outside limits |  | Yes | Immediate | Yes | Alarm | Warning | event | evt_byp_freqErr | Bypass Frequency Error | tag=nxlEvents:EventID24 | With the bypass input voltage above a minimum threshold, the bypass frequency is outside a specified percentage of nominal.Becomes inactive when the bypass frequency is inside a specified percentage of nominal.NOTE: If this event is active, then the inverter is not synchronized with the bypass source. Conversely, if this event is inactive it does not imply the inverter is synchronized with the bypass source.See 'evt_byp_unavail'.
4176 | 301 | Battery switch open | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_bat_brkr01Open | Battery Circuit Breaker 1 Open | tag=nxlEvents:EventID182 | Battery cabinet 1 circuit breaker is open.Becomes inactive when breaker closes.
4179 | 301 | Battery switch open | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_bat_brkr02Open | Battery Circuit Breaker 2 Open | tag=nxlEvents:EventID186 | Battery circuit breaker 2 is open.Becomes inactive when breaker closes.
4182 | 301 | Battery switch open | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_bat_brkr03Open | Battery Circuit Breaker 3 Open | tag=nxlEvents:EventID190 | Battery circuit breaker 3 is open.Becomes inactive when breaker closes.
4185 | 301 | Battery switch open | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_bat_brkr04Open | Battery Circuit Breaker 4 Open | tag=nxlEvents:EventID194 | Battery circuit breaker 4 is open.Becomes inactive when breaker closes.
4188 | 301 | Battery switch open | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_bat_brkr05Open | Battery Circuit Breaker 5 Open | tag=nxlEvents:EventID198 | Battery circuit breaker 5 is open.Becomes inactive when breaker closes.
4191 | 301 | Battery switch open | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_bat_brkr06Open | Battery Circuit Breaker 6 Open | tag=nxlEvents:EventID200 | Battery circuit breaker 6 is open.Becomes inactive when breaker closes.
4194 | 301 | Battery switch open | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_bat_brkr07Open | Battery Circuit Breaker 7 Open | tag=nxlEvents:EventID202 | Battery circuit breaker 7 is open.Becomes inactive when breaker closes.
4197 | 301 | Battery switch open | X | Yes | 1 minute | Yes | Alarm | Warning | event | evt_bat_brkr08Open | Battery Circuit Breaker 8 Open | tag=nxlEvents:EventID204 | Battery circuit breaker 8 is open.Becomes inactive when breaker closes.
4200 | 233 | Battery charger inhibit |  | No |  | No | Normal | Normal | event | evt_bat_chargeInhibit | Battery Charging Inhibited | tag=nxlEvents:EventID265 | Battery charging is inhibited due to an external inhibit signal.Becomes inactive when the external inhibit signal clears, thus allowing normal battery charging.
4213 | 1111 | Emergency stop operated |  | Yes | 10 seconds | No | Severe Warning | Warning | event | evt_sys_outEPO | System Shutdown - EPO | tag=nxlEvents:EventID137; tag=nxlEvents:EventID301 | System shutdown due to Emergency Power Off (EPO).Becomes inactive when the EPO signal is not active.
4214 | 1864 | System Shutdown - REPO |  | Yes | 10 seconds | No | Severe Warning | Warning | event | evt_sys_outREPO | System Shutdown - REPO | tag=nxlEvents:EventID138 | System shutdown due to Remote Emergency Power Off (REPO).Becomes inactive when the remote EPO signal is not active.
4215 | 607 | Output load not supplied |  | Yes | Immediate | Yes | Alarm | Severe Warning | event | evt_sys_outOff | System Output Off |  | Summary event that indicates that the output is off. The system output is defined as the critical bus supporting the load.Becomes inactive when the output is on.
4217 | 545 | Transfer to bypass inhibited | X | No |  | No | Normal | Normal | event | evt_byp_manXfrInhibited | Bypass - Manual Xfr Inhibited | tag=nxlEvents:EventID19 | Manual transfer from inverter to bypass is inhibited. Becomes active when operating on inverter and manual transfer to bypass is not permitted. Becomes inactive when manual transfer to bypass is permitted.
4218 | 505 | Reserve inhibited |  | Yes | 10 minutes | No | Warning | Normal | event | evt_byp_manReXfrInhibited | Bypass - Manual Rexfr Inhibited | tag=nxlEvents:EventID20 | Manual transfer from bypass to inverter is inhibited. Becomes active when operating on bypass and manual transfer to inverter is not permitted. Becomes inactive when manual transfer to inverter is permitted.
4219 | 315 | High battery temperature | X | Yes | 1 minute | Yes | Severe Warning | Severe Warning | event | evt_bat_tempOver | Battery Over Temperature | tag=nxlEvents:EventID36;tag=nxlEvents:EventID228 | A battery temperature is above a threshold.It becomes inactive when the battery temperature is below the activation threshold. Some products may have hysterisis for clearing the event.Raptor Specific - Becomes inactive when the battery temperature has decreased to a specified percentage of a specified setting or Battery Temperature setting is disable, the breaker is allowed to close.
4220 | 1654 | Battery maintenance recommended | X | No |  | No | Normal | Normal | event | evt_bat_monitor01Ext | Battery - External Monitor 1 | tag=nxlEvents:EventID304 | External battery monitor 1 indicates battery maintenance is required.Becomes inactive when the external monitor 1 signal clears.
4221 | 1654 | Battery maintenance recommended | X | No |  | No | Normal | Normal | event | evt_bat_monitor02Ext | Battery - External Monitor 2 | tag=nxlEvents:EventID303 | External battery monitor 2 indicates battery maintenance is required.Becomes inactive when the external monitor 2 signal clears.
4222 | 1832 | Ground Over current |  | No |  | No | Normal | Normal | event | evt_bat_groundFault | Battery Ground Fault | tag=nxlEvents:EventID297 | Battery system ground fault amperage exceeds the threshold. The battery system is defined to include all of the batteries in the system.Becomes inactive when ground fault amperage returns to normal levels.
4230 | 1865 | System Output Low Power Factor |  | No |  | No | Normal | Normal | event | evt_sys_outLowPwrFactor | System Output Low Power Factor | tag=nxlEvents:EventID108 | The system output power factor is low, resulting in reduced load capacity.This event is active when any output phase load current is above a threshold and the output power factor is below a threshold.Becomes inactive when the power factor increases above a threshold, or the load current decreases below a threshold thus making the power factor measurement inaccurate.NOTE: The load current threshold differentiates the point where accurate power factor measurements are possible.
4233 | 436 | Inverter fault |  | Yes | 10 seconds | Yes | Alarm | Warning | event | evt_inv_failure | Inverter Failure | tag=nxlEvents:EventID49 | Inverter failure - inverter output is off.This summary event is based on the detection of at least one inverter fault, which may include but is not limited to: inverter overvoltage, inverter undervoltage, inverter phase A fault, inverter phase B fault, inverter phase C fault, inverter DC fuse fail and inverter output fuse fail.Becomes inactive when all applicable inverter faults clear.
4234 | 474 | Inverter overload fault | X | Yes | 1 minute | Yes | Normal | Normal | event | evt_inv_overloadPhsA | Inverter Overload Phase A | tag=nxlEvents:EventID54 | Inverter is operating with an overload on phase A.Phase A of the inverter power limit (power draw and/or amperage draw) has been exceeded.Becomes inactive when phase A of the inverter is no longer overloaded.
4235 | 474 | Inverter overload fault | X | Yes | 1 minute | Yes | Normal | Normal | event | evt_inv_overloadPhsB | Inverter Overload Phase B | tag=nxlEvents:EventID55 | Inverter is operating with an overload on phase B.Phase B of the inverter power limit (power draw and/or amperage draw) has been exceeded.Becomes inactive when phase B of the inverter is no longer overloaded.
4236 | 474 | Inverter overload fault | X | Yes | 1 minute | Yes | Normal | Normal | event | evt_inv_overloadPhsC | Inverter Overload Phase C | tag=nxlEvents:EventID56 | Inverter is operating with an overload on phase C.Phase C of the inverter power limit (power draw and/or amperage draw) has been exceeded.Becomes inactive when phase C of the inverter is no longer overloaded.
4237 | 416 | Inverter inhibited |  | Yes | 10 seconds | Yes | Warning | Normal | event | evt_inv_restartInhibitExt | Inverter Inhibit - External |  | Restart of the inverter is inhibited by an external signal.Becomes inactive when the external signal has been cleared.
4270 | 6 | User input 1 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact01 | Input Contact 01 |  | The external input contact 1. It is either active or inactive.Becomes inactive when the external signal is not active.
4271 | 7 | User input 2 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact02 | Input Contact 02 |  | The external input contact 2. It is either active or inactive.Becomes inactive when the external signal is not active.
4272 | 8 | User input 3 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact03 | Input Contact 03 |  | The external input contact 3. It is either active or inactive.Becomes inactive when the external signal is not active.
4273 | 9 | User input 4 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact04 | Input Contact 04 |  | The external input contact 4. It is either active or inactive.Becomes inactive when the external signal is not active.
4274 | 10 | User input 5 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact05 | Input Contact 05 |  | The external input contact 5. It is either active or inactive.Becomes inactive when the external signal is not active.
4275 | 11 | User input 6 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact06 | Input Contact 06 |  | The external input contact 6. It is either active or inactive.Becomes inactive when the external signal is not active.
4276 | 12 | User input 7 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact07 | Input Contact 07 |  | The external input contact 7. It is either active or inactive.Becomes inactive when the external signal is not active.
4277 | 13 | User input 8 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact08 | Input Contact 08 |  | The external input contact 8. It is either active or inactive.Becomes inactive when the external signal is not active.
4278 | 14 | User input 9 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact09 | Input Contact 09 |  | The external input contact 9. It is either active or inactive.Becomes inactive when the external signal is not active.
4279 | 15 | User input 10 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact10 | Input Contact 10 |  | The external input contact 10. It is either active or inactive.Becomes inactive when the external signal is not active.
4280 | 16 | User input 11 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact11 | Input Contact 11 |  | The external input contact 11. It is either active or inactive.Becomes inactive when the external signal is not active.
4281 | 17 | User input 12 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact12 | Input Contact 12 |  | The external input contact 12. It is either active or inactive.Becomes inactive when the external signal is not active.
4282 | 18 | User input 13 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact13 | Input Contact 13 |  | The external input contact 13. It is either active or inactive.Becomes inactive when the external signal is not active.
4283 | 1866 | Input Contact 14 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact14 | Input Contact 14 |  | The external input contact 14. It is either active or inactive.Becomes inactive when the external signal is not active.
4284 | 1867 | Input Contact 15 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact15 | Input Contact 15 |  | The external input contact 15. It is either active or inactive.Becomes inactive when the external signal is not active.
4285 | 1868 | Input Contact 16 |  | No |  | No | Normal | Normal | event | evt_ext_inpContact16 | Input Contact 16 |  | The external input contact 16. It is either active or inactive.Becomes inactive when the external signal is not active.
4286 | 1233 | Current limit (phase 1) over threshold 1 alarm |  | Yes | 10 minutes | Yes | Severe Warning | Severe Warning | event | evt_sys_userOutAmpOverPhsA | Output Amp Over User Limit-Phs A | tag=nxlEvents:EventID163 | The phase A load has exceeded the user amperage threshold. This does not necessarily mean that the unit is overloaded.Becomes inactive when load is below the thresold.
4287 | 1235 | Current limit (phase 1) over threshold 2 alarm |  | Yes | 10 minutes | Yes | Severe Warning | Severe Warning | event | evt_sys_userOutAmpOverPhsB | Output Amp Over User Limit-Phs B | tag=nxlEvents:EventID164 | The phase B load has exceeded the user amperage threshold. This does not necessarily mean that the unit is overloaded.Becomes inactive when load is below the thresold.
4288 | 1237 | Current limit (phase 1) over threshold 3 alarm |  | Yes | 10 minutes | Yes | Severe Warning | Severe Warning | event | evt_sys_userOutAmpOverPhsC | Output Amp Over User Limit-Phs C | tag=nxlEvents:EventID165 | The phase C load has exceeded the user amperage threshold. This does not necessarily mean that the unit is overloaded.Becomes inactive when load is below the thresold.
4290 | 408 | Inhibited due to overload timeout |  | Yes | 1 minute | Yes | Alarm | Severe Warning | event | evt_inv_shutdownOverload | Inverter Shutdown - Overload | tag=nxlEvents:EventID57 | The inverter has shutdown due to a sustained overload.This event does not indicate if the load has been dropped or if the load has been transfered to bypass.At least one phase of the inverter power dissipation limit has been exceeded (Power or RMS current vs time curve). Generally, the UPS will take action to protect the inverter from the overload condition.Becomes inactive when transfer to inverter is permitted or if system is restarted.
4294 | 175 | High input air temperature |  | No |  | Yes | Severe Warning | Severe Warning | event | evt_sys_inletAirOverTemp | Inlet Air Over Temperature | See 'Raptor_ERS_Events.doc' in Perforce folder '\Raptor\ProjectManagement\Requirements' - Event ID 206 | The inlet air temperature exceeds a threshold.Becomes inactive when the temperature drops below the threshold.
4295 | 273 | Rectifier fault |  | Yes | 10 minutes | Yes | Alarm | Warning | event | evt_rct_failure | Rectifier Failure | tag=nxlEvents:EventID9 | Rectifier failure - rectifier is off.Summary event based on the detection of at least one of the rectifier faults. The possible faults include, but are not limited to the following: Battery Overcharge, DC Overvoltage Steady State, DC Overvoltage Transient, DC Undervoltage Steady State, Rectifier Delta/Wye Current Imbalance, Delta Rectifier Fuse Fail, Wye Rectifier Fuse Fail, Rectifier Sync Loss, Input Current Imbalance, Input Filter Fuse Failure, etc.Becomes inactive where all rectifier faults have cleared.
4296 | 208 | Rectifier inhibit |  | No |  | No | Warning | Warning | event | evt_rct_inhibitExt | Rectifier Operation Inhibit-Ext | tag=nxlEvents:EventID279 | The operation of the rectifier is inhibited by an external signal.Becomes inactive when the external signal has been cleared.
4298 | 659 | Output load supplied by bypass |  | Yes | Immediate | Yes | Warning | Warning | event | evt_sys_loadOnBypass | UPS Output on Bypass | tag=nxlEvents:EventID106 | The output power is supplied by the bypass. It becomes inactive when not on bypass.
4299 | 606 | Output load supplied through maintenance bypass |  | Yes | 1 minute | No | Normal | Normal | event | evt_sys_loadOnMaintBypass | Output Load on Maint. Bypass | tag=nxlEvents:EventID107 | The output power is supplied by the maintenance bypass. It becomes inactive when not on maintenance bypass.Raptor (NXL) Specific - Event is active when Maintenance Bypass Breaker (MBB) Closed (144739), Maintenance Bypass Isolator (QBP) Closed (144731), or Maintenance Isolator (Q3) Closed (144718) is active. Event is inactive when Maintenance Bypass Breaker (MBB) Open (144740), Maintenance Bypass Isolator (QBP) Open (144734), or Maintenance Isolator (Q3) Open (144716) are active.
4300 | 71 | Liebert communication fault | X | Yes | 1 minute | No | Normal | Normal | event | evt_sys_internalCommFailure | Internal Communications Failure | tag=nxlEvents:EventID285 | The control has detected a communication failure of a device on the internal communication bus. Summary event that indicates that there is an internal communication failure.Becomes inactive when all internal communication problems clear.Raptro Specific - Possible causes for this include, but are not limited to, the following:HMI Communication Failure, Static Bypass Switch System Failure, External Interface Communication, Fan Interface Board 1 Communication Failure, Fan Interface Board 2 Communication Failure, Fan Interface Board 3 Communication Failure, Fan Interface Board 4 Communication Failure, Programmable Relay Board #1 Communication Failure, Programmable Relay Board #2 Communication Failure, Input Contact Isolation #1 Communication Failure, Input Contact Isolation #2 Communication Failure, MBD/BCB Communication Failure, MBD 1/BIS 1 Communication Failure, MBD 2/BIS 2 Communication Failure, MBD 3/BIS 3 Communication Failure, 4/BIS 4 Communication Failure, MBD 5/BIS 5 Communication Failure, BIS 6 Communication Failure, BIS 7 Communication Failure, BIS 8 Communication Failure, Remote Alarm Status Panel Interface Communication Failure, etc.
4308 | 323 | Dc earth fault | X | No |  | No | Warning | Warning | event | evt_dcb_groundFaultPos | DC Bus Ground Fault - Positive | tag=nxlEvents:EventID295 | The positive DC link has a fault to ground. Ground fault current has been detected.Becomes inactive when the positive link ground fault current is no longer detected.
4309 | 323 | Dc earth fault | X | No |  | No | Warning | Warning | event | evt_dcb_groundFaultNeg | DC Bus Ground Fault - Negative | tag=nxlEvents:EventID296 | The negative DC link has a fault to ground. Ground fault current has been detected.Becomes inactive when the negative link ground fault current is no longer detected.
4310 | 419 | Over temperature |  | Yes | 1 minute | Yes | Warning | Warning | event | evt_sys_overTemperature | Equipment Over Temperature |  | Equipment over temperature.Summary event based on the detection of at least one temperature exeeding a threshold. The temperatures may include but are not limited to the following:Outlet Air Over Temperature,Rectifier Heatsink Over Temperature,Inverter Heatsink Over Temperature,Static Bypass Switch Heatsink Over Temperature,SSS Heatsink Over TemperatureBecomes inactive when all temperatures return to normal operating range.
4315 | 1219 | Generator on load |  | No |  | Yes | Normal | Normal | event | evt_sys_inpOnGenerator | On Generator | tag=nxlEvents:EventID125 | A generator is supplying the power to the system.Becomes inactive when the generator is not supplying the system power.Also see 'st_sys_inpSource'.
4316 | 1869 | Auto Restart In Progress |  | No |  | No | Warning | Warning | event | evt_sys_autoRestartInProgress | Auto Restart In Progress | tag=nxlEvents:EventID300 | Auto restart is in progress. The following conditions must meet: with Auto Restart enabled and Battery Low Shutdown active and Auto Restart Failed is not active, Input Contact Interface 1 (Channel #4) is active or Input Contact Interface 1 (Channel #5) is active or Input Contact Interface 1 (Channel #6) (128107) is active.Becomes inactive when auto restart completes or fails.
4317 | 1870 | Auto Restart Inhibited - Ext |  | No |  | No | Warning | Warning | event | evt_sys_autoRestartInhibitExt | Auto Restart Inhibited - Ext | tag=nxlEvents:EventID299 | Auto restart inhibited due to an external signal.Becomes inactive when the external signal clears.
4323 | 1679 | Battery test failed |  | No |  | Yes | Normal | Normal | event | evt_bat_testFailed | Battery Test Failed | tag=nxlEvents:EventID151 | Battery testing has been completed and failed.Raptor Specific - This event is latched and must be reset by the operator.
4325 | 1871 | Backfeed Breaker Open |  | No |  | No | Warning | Warning | event | evt_byp_backfeedBrkrOpen | Backfeed Breaker Open | tag=nxlEvents:EventID109 | The backfeed breaker is in the open position.It becomes inactive when the bypass backfeed breaker closed.
4382 | 1845 | System Input Current Imbalance |  | Yes | 1 minute | No | Normal | Normal | event | evt_sys_inpCurrentImbal | System Input Current Imbalance | tag=nxlEvents:EventID8 | The RMS rectifier input currents are imbalanced and have reached the level to indicate a failure in the input circuit.Becomes inactive when the difference between any single input phase current and the average of all input phase currents has returned to normal.Raptor (NXL) Specific - Input current levels are above 30% of nominal and all three phase voltages are within 5% of each other and there is a difference of less than 15% between any single input phase current and the average of all input phase currents.
4383 | 543 | Bypass off |  | Yes | 1 minute | No | Normal | Normal | event | evt_byp_remoteOffExt | Bypass Static Switch Off Extrnl | tag=nxlEvents:EventID281 | Bypass static switch is off due to the state of an external signal. The event becomes inactive when the external signal is not active.Raptor Specific-The remote bypass static switch off input channel has an external contact in the true condition. This is an LEU/LAP option only. LNA does not plan to use Remote Off Bypass Static Switch signal.With the Remote On/Off Operation (136789) setting Enabled" and Remote Off - Bypass Static Switch (143302) event active, the bypass static switch shall be inhibited from operating.When the Remote Off - Bypass Static Switch (143302) event is inactive, the bypass static switch shall start automatic restart operation if all the conditions for operation are acceptable."
4389 | 642 | Output general fail |  | Yes | Immediate | Yes | Alarm | Severe Warning | event | evt_sys_outFault | System Output Fault | tag=nxlEvents:EventID62 | Summary event based on the detection of at least one of the following faults: Output Overvoltage, Output Undervoltage, Output Over/Under Frequency.Becomes inactive when all causal faults have cleared.
4390 | 413 | Inverter stopped manually |  | Yes | Immediate | Yes | Alarm | Severe Warning | event | evt_inv_offExt | Inverter Off - External | See 'Raptor_ERS_Events.doc', Event ID 280 | Inverter is off (operation is inhibited) due to external signal state. The event remains active until the external signal is deasserted.RAPTOR SPECIFIC: This is an LEU/LAP option only. LNA does not plan to use this signal and shall not assert this event.With the Remote On/Off Operation (136789) setting Enabled" and when Remote Off - Inverter (142376) event active, theinverter shall be inhibited from operating. If the load is connected to the inverter the load shall be transfered tobypass if conditions for transfer are acceptable. If conditions for transfer are not acceptable the load shall be deenergized.When the Remote Off - Inverter (142376) event is inactive, the inverter shall start operation if all the conditions foroperation are acceptable. If the load is connected to the bypass source through the bypass static switch an automaticretransfer of the load to the inverter shall occur. If the bypass static switch is deenergized, the inverter shallconnected to the load at full voltage."
4391 | 445 | Inverter static switch in short circuit |  | Yes | 1 minute | No | Normal | Normal | event | evt_inv_ssSCRShort | Inverter Static Switch SCR Short | tag=nxlEvents:EventID314 | The system has detected a short across one or more inverter static switch Silicon Controlled Rectifiers. Once asserted, the system requires service to clear the event.Raptor Specific - This event applies to LEU/LAP models. LNA models do not have Inverter Static Switch. This event is unrecoverable.
4440 | 1600 | One or more fuses blown |  | Yes | 1 minute | No | Normal | Normal | event | evt_sys_fuseFailure | Fuse Failure | tag=nxlEvents:EventID286 | A summary event indicating one or more fuse failures. This is set when a fuse failure occurs, which may include but not limited to: rectifier fuse, input filter fuse, output fuse, inverter fuse, output filter fuse, bypass fuse, etc.Becomes inactive when all causal faults have cleared.
4441 | 71 | Liebert communication fault | X | Yes | 1 minute | No | Normal | Normal | event | evt_sys_controllerError | System Controller Error | tag=nxlEvents:EventID287 | System controller internal error. Summary event based on the detection of one or more controller faults. Becomes inactive when all causal faults have cleared. RAPTOR SPECIFIC: at least one of the following faults: DSP Communications Failure, Control DSP Failure
4442 | 1142 | Mains breaker/contactor fail to open |  | Yes | 1 minute | Yes | Severe Warning | Severe Warning | event | evt_sys_breakerOpenFail | System Breaker(s) Open Failure | tag=nxlEvents:EventID288 | One or more breakers in the system failed to open. Summary event based on the detection of one or more breakers that failed to open. The breakers in question include, but are not limited to: system output breaker, input breaker, battery cabinet breaker, inverter breaker, etc.Becomes inactive when all causal faults have leared.RAPTOR SPECIFIC: Backfeed Breaker Open Fail (138061), System Output Breaker Open Fail (138063), Rectifier Input Breaker (CB1) Open Fail (138981), Bypass Breaker (CB3) Open Fail (127643), Module Battery Disconnect Open Fail (144724), Battery CB 1 Open Fail (138976), Battery CB 2 Open Fail (138977), Battery CB 3 Open Fail (138978), Battery CB 4 Open Fail (138979), Battery CB 5 Open Fail (138980), Inverter Output Breaker (CB2) Open Fail (138060)Becomes inactive when all causal faults have cleared.
4726 | 108 | Maintenance service recommended |  | No |  | No | Normal | Normal | event | evt_sys_serviceReq | Service Required | tag=nxlEvents:EventID240 | Unit requires servicing. The event is generally deactivated by manual reset or act of service.The annunciation of this event may optionally be modified by:st_sys_serviceReqEnablest_sys_serviceReqTypeiCOM Specific: The event will not be activated unless it is enabled and the event condition is true for the full event delay period.
4740 | 74 | Battery Test not Allowed |  | No |  | No | Normal | Normal | event | evt_bat_autoTestInhibit | null | tag=nxlEvents:EventID259 | Automatic (scheduled) battery tests are inhibited. This is asserted if an automatic battery test is attempted and the conditions for the test are not acceptable.Becomes inactive when a battery test is successfully started (automatic or manual).
4741 | 280 | Automatic Battery test |  | No |  | No | Normal | Normal | event | evt_bat_selfTest | Battery Self Test | tag=nxlEvents:EventID134 | Battery self test is in progress. A battery test is in process and will continue until the test completes or terminates due to an external event.Becomes inactive when the test completes or terminates due to an external event.
4742 | 326 | End of discharge |  | No |  | Yes | Severe Warning | Severe Warning | event | evt_bat_lowShutdown | Battery Low Shutdown | tag=nxlEvents:EventID32 | Battery disconnect due to end-of-discharge. This event is annunciated when a battery end-of-discharge occurs. There is no automatic clearing action for this event unless auto restart feature is enabled and battery charging resumes. NOTE: See the event 'evt_sys_outOffEoD'; evt_sys_outOffEoD is the preferred event for a UPS and should be used to indicate that the output power was dropped due to a low battery condition. However, for systems that can reach an EoD condition, and still maintain output power beyond this event, then the use of this event is appropriate. For example, for a dual power source UPS, it is possible that the mains are lost while the bypass power source is still available. For such a case, it is possible for the system to transfer to bypass after the EoD and maintain the system output power.
4747 | 107 | Output air temperature sensor fault |  | Yes | 1 hour | No | Warning | Warning | event | evt_sys_equipTempSensorFailed | Equipment Temperature Sensor Fail | tag=nxlEvents:EventID217 | A temperature sensor is reporting a value outside of sensor operating range or values inconsistent with a properly operating sensor.
4749 | 166 | Fan failure | X | No |  | No | Warning | Warning | event | evt_sys_fanFailureRedundant | System Fan Failure - Redundant | tag=nxlEvents:EventID154 | One fan failure is present. Summary event based on the detection of no more than one of many fan failures.Becomes inactive when All fans are operational or a Multiple Fan Failure event is active.
4750 | 166 | Fan failure | X | No |  | No | Warning | Warning | event | evt_sys_fanMultiple | Multiple Fan Failure | tag=nxlEvents:EventID293 | More than one fan failure is present. This is a summary event based on the detection of more than one fan failure.For Raptor/NXL, an FIB (Fan Interface Board) may have stopped communicating.Becomes inactive when the fan failures corrected.
4753 | 43 | MUN fault |  | Yes | 1 minute | No | Alarm | Warning | event | evt_sys_mainControllerFault | Main Controller Fault | tag=nxlEvents:EventID219 | The redundant system has detected that the main UPS control has failed.Raptor/NXL specific - The failure is detected via a watchdog" timeout mechanism.Event Recovery - Control power must be cycled. It may also require a reset to be issued from the front panel display."
4754 | 1140 | Mains breaker/contactor fail to close |  | Yes | 1 minute | No | Normal | Normal | event | evt_sys_breakerCloseFail | System Breaker(s) Close Failure | tag=nxlEvents:EventID289 | Summary event based on the detection of at least one of the following faults:System Output Breaker Close Fail (138062)Rectifier Input Breaker (CB1) Close Fail (138046)Bypass Breaker (CB3) Close Fail (127651)Module Battery Disconnect Close Fail (144725)Battery CB 1 Close Fail (138049)Battery CB 2 Close Fail (138050)Battery CB 3 Close Fail (138051)Battery CB 4 Close Fail (138052)Battery CB 5 Close Fail (138053)Inverter Output Breaker (CB2) Close Fail (138059).Becomes inactive when all causal faults have cleared.
4755 | 1872 | Input Filter Cycle Lock |  | No |  | No | Normal | Normal | event | evt_sys_inpFilterCycleLock | Input Filter Cycle Lock | tag=nxlEvents:EventID290 | The input filter disconnect has been opened too many times within a period of time, exceeding a maximum cycle count, and is now locked out.Becomes inactive when Input Passive Filter disconnect closes.NXL Specific: The input filter disconnect has opened more than nine times in the previous one hour.Becomes inactive when Input Passive Filter Close command is active.
4823 | 1691 | Parallel communication fault |  | No |  | No | Severe Warning | Severe Warning | event | evt_mms_parCommWarn | Parallel Comm Warning | tag=nxlEvents:EventID320 | One of the paralleling control communication busses is no longer communicating within the system. This event recovers when all of the communications busses are communicating.
4824 | 71 | Liebert communication fault | X | Yes | 1 minute | No | Normal | Normal | event | evt_mms_sysCommFail | System Comm Fail | tag=nxlEvents:EventID321 | The control has detected a communication failure of a device on the multi-module communication bus. Event will recover when all causal faults have cleared.
4825 | 1635 | UPS loss of redundancy |  | Yes | 1 minute | No | Severe Warning | Severe Warning | event | evt_mms_lossRedundancy | Loss of Redundancy | tag=nxlEvents:EventID330 | The multi-module system has been programmed as a redundant, but has an insufficient number of modules to provide the redundancy. (event 330)
4826 | 1880 | Parallel Bypass Static Switch Start Inhibited |  | No |  | No | Normal | Normal | event | evt_mms_bpssStartInhibit | BPSS Startup Inhibit | tag=nxlEvents:EventID333 | The Bypass Static Switch Startup is Inhibited because there are not enough bypasses to support the rated capacity. Will recover when there are a sufficient number of bypasses to support the rated capacity.Raptor Specific:This only applies to 1+N systems.
4827 | 1879 | Parallel BypassTransfer Inhibit |  | No |  | No | Warning | Warning | event | evt_mms_xfer_inhibit | MMS Transfer Inhibit | tag=nxlEvents:EventID101 | In a Multi-Module System, the critical load can not be manually transferred from inverter to bypass. Recovers when the conditions preventing the transfer are resolved.Raptor Specific:With the collective on UPS, Module Output Breaker (MOB) Open is active or Output Isolator (QE) Open is active or Manual Transfer Inhibit is active or not enough BPSSs are available to support the measured load or any module's BPSS is connected to the collective.
4828 | 1873 | Parallel Bypass Retransfer Inhibit |  | No |  | No | Warning | Warning | event | evt_mms_rexfer_inhibit | MMS Retransfer Inhibit | tag=nxlEvents:EventID112 | In a Multi-Module System, the critical load can not be manually retransferred from bypass to inverter. Recovers when the conditions preventing the retransfer are resolved.Raptor Specific:With the collective not on UPS, Module Output Breaker (MOB) Open is active or Output Isolator (QE) Open is active or Manual Retransfer Inhibit is active or not enough inverters are available to support the measured load or any module's inverter is connected to the collective.
4830 | 1874 | Parallel Loss of Sync Pulse |  | No |  | No | Normal | Normal | event | evt_mms_syncLoss | MMS Loss of Sync Pulse | tag=raptorERS:event126 | A module in a MMS has detected that there is no longer a sync pulse being generated. Recovery from this alarm involves recycling power on all modules in the collective.
4831 | 1689 | Parallel system overload |  | Yes | 1 minute | No | Severe Warning | Severe Warning | event | evt_mms_systemOverload | MMS Overload | tag=raptorERS:event140 | Multi-Module System Overload. One or more modules in a multi-module system is reporting an overload on at least one phase. Cleared when the overload condition is removed from all modules.
4834 | 1696 | Parallel load on battery |  | Yes | 1 minute | No | Warning | Warning | event | evt_mms_onBatt | MMS On Battery | tag=raptorERS:event191 | The number of modules on battery exceeds the number of redundant modules on line.. Will clear when no modules on battery. @todo investigate recovery
5144 | 641 | Output Frequency outside limits |  | Yes | immediate | Yes | Severe Warning | Severe Warning | event | evt_sys_outOfUf | Output Of/Uf | tag=nxlEvents:EventID63 | Output frequency differs from the nominal by more than a specified amount.
5456 | 1875 | ECO Mode Active |  | No |  | No | Normal | Normal | event | evt_sys_ecoModeActive | ECO Mode Active | tag=raptorERS:event205 | ECO Mode is acitve
5561 | 1876 | LBS Active - Master |  | No |  |  | Normal | Normal | event | evt_sys_lbsMaster | LBS Active - Master | tag=nxlEvents:EventID239 | This UPS system has been selected as the functional Master Load Bus Synchronization (LBS) system.
5562 | 1877 | LBS Active - Slave |  | No |  |  | Normal | Normal | event | evt_sys_lbsSlave | LBS Active - Slave | tag=nxlEvents:EventID308 | This status message informs the user that the Load Bus Sync (LBS) is active and this UPS system is synchronized to the output bus of the UPS system that has been selected as the Master LBS system.This status message is self-clearing. When the condition is no longer present, the alarm and any control activity tied to the alarm reverts to normal.NXL specific - This event replaced 'evt_sys_lbsActive'.
5768 | 133 | Temperature too high in device |  | Yes | 1 minute |  | Severe Warning | Warning | event | evt_sys_outletOverTempLimit | Outlet Air Overtemperature Limit | tag=nxlEvents:EventID207 | The difference between the maximum outlet air temperature and the inlet air temperature exceeds a specified value.
5769 | 1878 | EMO Shutdown |  | Yes | immediate |  | Severe Warning | Warning | event | evt_sys_emoShutdown | EMO Shutdown | tag=nxlEvents:EventID301 | The EMO signal is active, the device has commenced its emergency shutdown sequence.The EMO will shut down the module, but leave the overall system in bypass. Becomes inactive when the EMO signal is not active.NXL Specific:Device has intiated the following sequence: automatic transfer to bypass, turn off inverter, open output disconnect device, turn off rectifier, trip all battery CBs and open input disconnect device.
4871 | 325 | Battery normal |  | No |  | No | Normal | Normal | =2 | st_bat_upsBattStatus | UPS battery1 status
4871 | 306 | Flat battery |  | Yes | 1 minute | No | Severe Warning | Severe Warning | =4 | st_bat_upsBattStatus | UPS battery1 status
4746 | 448 | Inverter on |  | No |  | Yes | Normal | Normal | =1 | st_inv_opState | Inverter On/Off State
4746 | 415 | Inverter off |  | Yes | 1 minute | Yes | Alarm | Warning | 0 | st_inv_opState | Inverter On/Off State
4299 | 627 | Maintenance Bypass switch closed |  | Yes | 1 minute | Yes | Alarm | Warning | event | evt_sys_loadOnMaintBypass | Output Load on Maint.Bypass
4123 | 126 | Ups Warning |  | Yes | 1 minute | No | Warning | Warning | 8 | st_sys_status | System Status
4123 | 1106 | Warning Alarm active |  | Yes | 1 minute | No | Warning | Warning | 16 | st_sys_status | System Status
4872 | 660 | Output load supplied by inverter |  | No |  | Yes | Normal | Normal | =3 | st_sys_upsOutputSource | UPS Output Source
4872 | 621 | Output load supplied by battery |  | Yes | Immediate | Yes | Warning | Warning | =5 | st_sys_upsOutputSource | UPS Output Source
4223 | 1885 | Output power over 85% for one or more phase | X | No |  | Yes | Warning | Warning | >85 | val_sys_pct_outPwrPhsAN | System Output Pct Power Phase A
4224 | 1885 | Output power over 85% for one or more phase | X | No |  | Yes | Warning | Warning | >85 | val_sys_pct_outPwrPhsBN | System Output Pct Power Phase B
4225 | 1885 | Output power over 85% for one or more phase | X | No |  | Yes | Warning | Warning | >85 | val_sys_pct_outPwrPhsCN | System Output Pct Power Phase C
| 647 | Load on bypass warning | SMS | Yes | Immediate | No | Alarm | Warning | same as ev 659 datapoint 4298
| 270 | Emergency primary mains failure | SMS | Yes | Immediate | No | Alarm | Warning | same as ev 202 datapoint 4122
| 243 | Primary Mains power recovered | SMS | Yes | Immediate | No | Alarm | Warning | recover from ev 270
| 572 | Emergency reserve supply failure | SMS | Yes | Immediate | No | Alarm | Warning | same as ev 593 datapoint 4135

## NXl_2199-meas
PointId | LifeId | Life Measures | DataType | DataScaling | DataOffset | Resolution | Min | Max | Unit Of Measure | Threshold Type | Threshold Value | PgmName | Point Label | EngReference | EngDescription
4097 | 90 | Mains L1-L2 voltage | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_sys_ep_inpRmsPhsAB | System Input RMS A-B |  | This is the system input RMS voltage between Phase A and Phase B. The system input is defined as the source of power (utility or mains) for the device.This data definition is intended to be used with devices that only have one system input. The system input for this data definition may be multi-phased. A system bypass input is NOT considered to be a second system input. For the system bypass input definition see val_byp_ep_inpRmsPhsAB.Do NOT use this data definition if the device has more that one system input. An example of a device that has more than one system input is the STS2.For a single system input 3-phase UPS, this data point is the RMS voltage between Phase A and Phase B of the utility (or mains) that supplies the UPS with power.Similarly, it is the RMS voltage between Phase A and Phase B of the utility that supplies power to an environmental or other unit.Raptor Specific - 3-phase input
4099 | 91 | Mains L2-L3 voltage | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_sys_ep_inpRmsPhsBC | System Input RMS B-C |  | This is the system input RMS voltage between Phase B and Phase C. The system input is defined as the source of power (utility or mains) for the device.This data definition is intended to be used with devices that only have one system input. The system input for this data definition may be multi-phased. A system bypass input is NOT considered to be a second system input. For the system bypass input definition see val_byp_ep_inpRmsPhsBC.Do NOT use this data definition if the device has more that one system input. An example of a device that has more than one system input is the STS2.For a single system input 3-phase UPS, this data point is the RMS voltage between Phase B and Phase C of the utility (or mains) that supplies the UPS with power.Similarly, it is the RMS voltage between Phase B and Phase C of the utility that supplies power to an environmental or other unit.Raptor Specific - 3-phase input
4101 | 92 | Mains L3-L1 voltage | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_sys_ep_inpRmsPhsCA | System Input RMS C-A |  | This is the system input RMS voltage between Phase C and Phase A. The system input is defined as the source of power (utility or mains) for the device.This data definition is intended to be used with devices that only have one system input. The system input for this data definition may be multi-phased. A system bypass input is NOT considered to be a second system input. For the system bypass input definition see val_byp_ep_inpRmsPhsCA.Do NOT use this data definition if the device has more that one system input. An example of a device that has more than one system input is the STS2.For a single system input 3-phase UPS, this data point is the RMS voltage between Phase C and Phase A of the utility (or mains) that supplies the UPS with power.Similarly, it is the RMS voltage between Phase C and Phase A of the utility that supplies power to an environmental or other unit.Raptor Specific - 3-phase input
4105 | 36 | Mains Frequency | DataUint16 | 1 | 0 | 1 | 0 | 65535 | Hz |  |  | val_sys_freq_inp | System Input Frequency |  | The system input frequency.This data definition is intended to be used with devices that only have one system input. The system input may be single, 2-phase or 3-phase. A system bypass input is NOT considered to be a second system input. For the system bypass input definition see val_byp_freq_inp.Do NOT use this data definition if the device has more that one system input. An example of a device that has more than one system input is the STS2.The system input is defined as the source of power (utility or mains) for the device.
4113 | 125 | Mains Current Ph1 | DataUint16 | 1 | 0 | 0 | 0 | 65535 | A AC |  |  | val_sys_ec_inpRmsPhsA | System Input RMS Current Phase A |  | The measured system input RMS current for Phase A.This data definition is intended to be used with devices that only have one system input. The system input may be single, 2-phase or 3-phase. A system bypass input is NOT considered to be a second system input.Do NOT use this data definition if the device has more that one system input. An example of a device that has more than one system input is the STS2.The system input is defined as the source of power (utility or mains) for the device.
4114 | 126 | Mains Current Ph2 | DataUint16 | 1 | 0 | 0 | 0 | 65535 | A AC |  |  | val_sys_ec_inpRmsPhsB | System Input RMS Current Phase B |  | The measured system input RMS current for Phase B.This data definition is intended to be used with devices that only have one system input. The system input may be single, 2-phase or 3-phase. A system bypass input is NOT considered to be a second system input.Do NOT use this data definition if the device has more that one system input. An example of a device that has more than one system input is the STS2.The system input is defined as the source of power (utility or mains) for the device.
4115 | 127 | Mains Current Ph3 | DataUint16 | 1 | 0 | 0 | 0 | 65535 | A AC |  |  | val_sys_ec_inpRmsPhsC | System Input RMS Current Phase C |  | The measured system input RMS current for Phase C.This data definition is intended to be used with devices that only have one system input. The system input may be single, 2-phase or 3-phase. A system bypass input is NOT considered to be a second system input.Do NOT use this data definition if the device has more that one system input. An example of a device that has more than one system input is the STS2.The system input is defined as the source of power (utility or mains) for the device.
4125 | 206 | Reserve L1-L2 voltage | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_byp_ep_inpRmsPhsAB | Bypass Input Voltage RMS A-B |  | DEFINITION:This is the bypass input RMS voltage between Phase A and Phase B. The bypass input is defined as the source of power (utility or mains) for the system bypass.This data definition is intended to be used with systems that only have one bypass input. The bypass input may be single, 2-phase or 3-phase.EXAMPLES:For a single bypass input 3-phase UPS, this data point is the RMS voltage between Phase A and Phase B of the utility (or mains) that supplies the UPS bypass with power.Raptor Specific - 3 or 4 phase bypass
4126 | 207 | Reserve L2-L3 voltage | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_byp_ep_inpRmsPhsBC | Bypass Input Voltage RMS B-C |  | DEFINITION:This is the bypass input RMS voltage between Phase B and Phase C. The bypass input is defined as the source of power (utility or mains) for the system bypass.This data definition is intended to be used with systems that only have one bypass input. The bypass input may be single, 2-phase or 3-phase.EXAMPLES:For a single bypass input 3-phase UPS, this data definition is the RMS voltage between Phase B and Phase C of the utility (or mains) that supplies the UPS bypass with power.Raptor Specific - 3 or 4 phase bypass
4127 | 208 | Reserve L3-L1 voltage | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_byp_ep_inpRmsPhsCA | Bypass Input Voltage RMS C-A |  | DEFINITION:This is the bypass input RMS voltage between Phase C and Phase A. The bypass input is defined as the source of power (utility or mains) for the system bypass.This data definition is intended to be used with systems that only have one bypass input. The bypass input may be single, 2-phase or 3-phase.EXAMPLES:For a single bypass input 3-phase UPS, this data definition is the RMS voltage between Phase C and Phase A of the utility (or mains) that supplies the UPS bypass with power.Raptor Specific - 3 or 4 phase bypass
4131 | 12 | Reserve Frequency | DataUint16 | 1 | 0 | 1 | 0 | 65535 | Hz |  |  | val_byp_freq_inp | Bypass Input Frequency |  | DEFINITION:The bypass input frequency.This data definition is intended to be used with systems that only have one bypass input. The bypass input may be single, 2-phase or 3-phase.The bypass input is defined as the source of power (utility or mains) for the system bypass.
4148 | 1 | Dc Voltage | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VDC |  |  | val_dcb_ep_dcBus | DC Bus Voltage |  | The voltage between the positive and negative terminals of the DC bus.
4149 | 4 | Dc Current | DataInt16 | 1 | 0 | 0 | -32768 | 32767 | A DC |  |  | val_dcb_ec_dcBus | DC Bus Current |  | The current at the battery input terminals. DC bus current can be either charging or discharging. In charging mode, the current will be a positive value. In discharging mode, the current will be a negative value.If there are multiple battery strings that comprise the system battery, then this current is for the system battery (i.e. it includes all of the batteries in the system).If a fly wheel is used instead of a battery, then this is the current flowing into or out of the fly wheel source.
4150 | 163 | Battery time remaining | DataUint16 | 1 | 0 | 0 | 0 | 65535 | min |  |  | val_bat_tm_remaining | Battery Time Remaining |  | The calculated available time on battery.NOTE: A UPS is expected to provide a battery time remaining value even when not operating on battery. However, if the system is not capable of providing this information, then use the FDM special value to indicate that the value is unavailable.
4153 | 159 | Estimated battery Charge | DataUint16 | 1 | 0 | 0 | 0 | 65535 |  |  |  | val_bat_pct_charge | Battery Percentage Charge |  | The percentage of battery charge. If the batteries charge long enough, this value should reach 100%. The parameter is NOT related to the age of the battery, which can effect the ability of the battery to hold as much energy as when it was new. See val_bat_wh_capacity.
4154 | 7 | Battery Voltage | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VDC |  |  | val_bat_ep_mainDisconnect | Battery Volts at Main Disconnect |  | The voltage between the most positive and the most negative battery terminals of the common battery disconnect. This disconnect isolates all batteries (or DC sources) from the system.
4159 | 212 | Battery Discharge Power | DataUint16 | 1 | 0 | 0 | 0 | 65535 | W |  |  | val_bat_pwr_discharge | Battery Discharge Power |  | Instantaneous battery power while discharging (DC volts times DC amps).
4201 | 198 | System Output Voltage RMS A-B | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_sys_ep_outRmsPhsAB | System Output Voltage RMS A-B |  | This is the system output RMS voltage between Phase A and Phase B. The system output is defined as the critical bus supporting the load.Raptor Specific - 3 or 4 phase output
4202 | 199 | System Output Voltage RMS B-C | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_sys_ep_outRmsPhsBC | System Output Voltage RMS B-C |  | This is the system output RMS voltage between Phase B and Phase C. The system output is defined as the critical bus supporting the load.Raptor Specific - 3 or 4 phase output
4203 | 200 | System Output Voltage RMS C-A | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_sys_ep_outRmsPhsCA | System Output Voltage RMS C-A |  | This is the system output RMS voltage between Phase C and Phase A. The system output is defined as the critical bus supporting the load.Raptor Specific - 3 or 4 phase output
4204 | 213 | System Output RMS Current Phs A | DataUint16 | 1 | 0 | 0 | 0 | 65535 | A AC |  |  | val_sys_ec_outRmsPhsA | System Output RMS Current Phs A |  | The system output RMS current for Phase A. The system output is defined as the critical bus supporting the load.
4205 | 214 | System Output RMS Current Phs B | DataUint16 | 1 | 0 | 0 | 0 | 65535 | A AC |  |  | val_sys_ec_outRmsPhsB | System Output RMS Current Phs B |  | The system output RMS current for Phase B. The system output is defined as the critical bus supporting the load.
4206 | 215 | System Output RMS Current Phs C | DataUint16 | 1 | 0 | 0 | 0 | 65535 | A AC |  |  | val_sys_ec_outRmsPhsC | System Output RMS Current Phs C |  | The system output RMS current for Phase C. The system output is defined as the critical bus supporting the load.
4207 | 23 | Output Frequency | DataUint16 | 1 | 0 | 1 | 0 | 65535 | Hz |  |  | val_sys_freq_out | System Output Frequency |  | The system output frequency. The system output is defined as the critical bus supporting the load.
4208 | 111 | Load apparent power | DataUint16 | 1 | 0 | 0 | 0 | 65535 | kW |  |  | val_sys_pwr_out | System Output Power |  | The sum total power of all system output phases. The system output is defined as the critical bus supporting the load.
4209 | 112 | Load real power | DataUint16 | 1 | 0 | 0 | 0 | 65535 | kVA |  |  | val_sys_ap_out | System Output Apparent Power |  | The sum total apparent power of all system output phases. The system output is defined as the critical bus supporting the load.
4210 | 216 | System Output Power Factor Phs A | DataInt16 | 1 | 0 | 2 | -32768 | 32767 |  |  |  | val_sys_na_outPwrFactPhsA | System Output Power Factor Phs A |  | The system output power factor of phase A. The system output is defined as the critical bus supporting the load.
4211 | 217 | System Output Power Factor Phs B | DataInt16 | 1 | 0 | 2 | -32768 | 32767 |  |  |  | val_sys_na_outPwrFactPhsB | System Output Power Factor Phs B |  | The system output power factor of phase B. The system output is defined as the critical bus supporting the load.
4212 | 218 | System Output Power Factor Phs C | DataInt16 | 1 | 0 | 2 | -32768 | 32767 |  |  |  | val_sys_na_outPwrFactPhsC | System Output Power Factor Phs C |  | The system output power factor of phase C. The system output is defined as the critical bus supporting the load.
4232 | 219 | Inverter Overload Time Remaining | DataUint16 | 1 | 0 | 0 | 0 | 65535 | sec |  |  | val_inv_tm_overloadRemaing | Inverter Overload Time Remaining |  | The calculated time remaining before inverter shutdown. The calculated time of inverter operation remaining for the present overload event.
4291 | 33 | Inlet Air temperature | DataInt16 | 1 | 0 | 0 | -32768 | 32767 | deg C |  |  | val_sys_temp_inletAir | Inlet Air Temperature |  | The temperature of the inlet air.This is measured using a sensor that is mounted near the air inlet and approximately measures the external air temperature. The air inlet provides most of the air used to dissipate execess heat in the system.
4385 | 20 | Output Voltage Ph1 | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_sys_ep_outRmsPhsAN | System Output Voltage RMS A-N | See Caliber Requirement 155037 in Raptor project. | This is the system output RMS voltage between Phase A and Neutral. The system output is defined as the critical bus supporting the load.
4386 | 21 | Output Voltage Ph2 | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_sys_ep_outRmsPhsBN | System Output Voltage RMS B-N | See Caliber Requirement 155038 in Raptor project. | This is the system output RMS voltage between Phase B and Neutral. The system output is defined as the critical bus supporting the load.
4387 | 22 | Output Voltage Ph3 | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_sys_ep_outRmsPhsCN | System Output Voltage RMS C-N | See Caliber Requirement 155039 in Raptor project. | This is the system output RMS voltage between Phase C and Neutral. The system output is defined as the critical bus supporting the load.
4801 | 220 | Parallel - Output Voltage RMS A-B | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_mms_ep_outRmsPhsAB | Multi-module System Output Voltage RMS A-B |  | The multi-module system output RMS voltage between Phase A and Phase B. The system output is defined as the critical bus supporting the load.Raptor specific:For 1+N this is averaged from the individual voltage measurementsFor N+1 this average voltage is measured directly.
4802 | 221 | Parallel - Output Voltage RMS B-C | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_mms_ep_outRmsPhsBC | Multi-module System Output Voltage RMS B-C |  | The multi-module system output RMS voltage between Phase B and Phase C. The system output is defined as the critical bus supporting the load.Raptor specific:For 1+N this is averaged from the individual voltage measurementsFor N+1 this average voltage is measured directly.
4803 | 222 | Parallel - Output Voltage RMS C-A | DataUint16 | 1 | 0 | 0 | 0 | 65535 | VAC |  |  | val_mms_ep_outRmsPhsCA | Multi-module System Output Voltage RMS C-A |  | The multi-module system output RMS voltage between Phase C and Phase A. The system output is defined as the critical bus supporting the load.Raptor specific:For 1+N this is averaged from the individual voltage measurementsFor N+1 this average voltage is measured directly.
4807 | 223 | Parallel - Sum of Output RMS Currents for Phase A | DataUint16 | 1 | 0 | 0 | 0 | 65535 | A AC |  |  | val_mms_ec_outRmsPhsA | Sum of MMS Output RMS Currents for Phase A |  | The sum of the System Output RMS currents Phs A. The system output is defined as the critical bus supporting the load.Raptor specific:For 1+N this is summed from the individual current measurementsFor N+1 this summed current is measured directly.
4808 | 224 | Parallel - Sum of Output RMS Currents for Phase B | DataUint16 | 1 | 0 | 0 | 0 | 65535 | A AC |  |  | val_mms_ec_outRmsPhsB | Sum of MMS Output RMS Currents for Phase B |  | The sum of the System Output RMS currents Phs B. The system output is defined as the critical bus supporting the load.Raptor specific:For 1+N this is summed from the individual current measurementsFor N+1 this summed current is measured directly.
4809 | 225 | Parallel - Sum of Output RMS Currents for Phase C | DataUint16 | 1 | 0 | 0 | 0 | 65535 | A AC |  |  | val_mms_ec_outRmsPhsC | Sum of MMS Output RMS Currents for Phase C |  | The sum of the System Output RMS currents Phs C. The system output is defined as the critical bus supporting the load.Raptor specific:For 1+N this is summed from the individual current measurementsFor N+1 this summed current is measured directly.
4810 | 226 | Parallel - Output Frequency | DataUint16 | 1 | 0 | 1 | 0 | 65535 | Hz |  |  | val_mms_freq_out | MMS Output Frequency | Caliber[136019] | The multi-module system output frequency. The system output is defined as the critical bus supporting the load.Raptor specific:For N+1 the frequency is measured at the system output terminalsFor 1+N the frequency is measured at the modules.
4811 | 205 | Parallel - Output Power | DataUint16 | 1 | 0 | 0 | 0 | 65535 | kW |  |  | val_mms_pwr_out | MMS Output Power |  | The total output power of the multi-module system.Raptor specific:For 1+N this is summed from the individual power measurementsFor N+1 the output power is measured directly.
4812 | 204 | Parallel - Output Apparent Power | DataUint16 | 1 | 0 | 0 | 0 | 65535 | kVA |  |  | val_mms_ap_out | MMS Output Apparent Power |  | The total output kVA (apparent power) of the multi-module system.Raptor specific:For 1+N this is summed from the individual power measurementsFor N+1 the output power is measured directly.
4813 | 227 | Parallel - Output Power Factor Phase A | DataInt16 | 1 | 0 | 2 | -32768 | 32767 |  |  |  | val_mms_na_outPwrFactPhsA | MMS Output Power Factor Phase A |  | The multi-module system output power factor for Phase A. The system output is defined as the critical bus supporting the load.Raptor specific:For 1+N this is derived from the individual power measurementsFor N+1 this is measured directly.
4814 | 228 | Parallel - Output Power Factor Phase B | DataInt16 | 1 | 0 | 2 | -32768 | 32767 |  |  |  | val_mms_na_outPwrFactPhsB | MMS Output Power Factor Phase B |  | The multi-module system output power factor for Phase B. The system output is defined as the critical bus supporting the load.Raptor specific:For 1+N this is derived from the individual power measurementsFor N+1 this is measured directly.
4815 | 229 | Parallel - Output Power Factor Phase C | DataInt16 | 1 | 0 | 2 | -32768 | 32767 |  |  |  | val_mms_na_outPwrFactPhsC | MMS Output Power Factor Phase C |  | The multi-module system output power factor for Phase C. The system output is defined as the critical bus supporting the load.Raptor specific:For 1+N this is derived from the individual power measurementsFor N+1 this is measured directly.

## life_events
0 | Events Data lost
1 | Service active
2 | Adjust time
3 | Ups connection lost
4 | Ups frame not correct
5 | Unit just supplied
6 | User input 1
7 | User input 2
8 | User input 3
9 | User input 4
10 | User input 5
11 | User input 6
12 | User input 7
13 | User input 8
14 | User input 9
15 | User input 10
16 | User input 11
17 | User input 12
18 | User input 13
19 | User relay output 1
20 | User relay output 2
21 | User relay output 3
22 | User relay output 4
23 | User relay output 5
24 | User relay output 6
25 | User relay output 7
26 | User relay output 8
27 | User relay output 9
28 | User relay output 10
29 | User relay output 11
30 | User relay output 12
31 | User output 13
32 | User output 14
33 | User output 15
34 | Configuration error
35 | Power history active
36 | Timekeeper battery low
37 | DSP locked
38 | Module Warning
39 | Module Fault
40 | Module Supplying Load
41 | Module Not Supplying Load
42 | CAN communication interrupted
43 | MUN fault
44 | reserved
45 | Bypass Reliability Level: Low
46 | Bypass Reliability Level: Medium-Low
47 | Bypass Reliability Level: Medium-High
48 | Bypass Reliability Level: High
49 | Trinergy or C.R. auto-disable
50 | reserved
51 | Operating Command Accepted: VFI
52 | Operating Command Accepted: VI
53 | Operating Command Accepted: VFD
54 | Operating Command Accepted: VFI and C.R.
55 | Unit Manual Control Mode
56 | Total Power Calculation Running
57 | C.R. Threshold Self Adapted
58 | Operating Command Request: VFI
59 | Operating Command Request: VI
60 | Operating Command Request: VFD
61 | Operating Command Request: VFI and C.R.
62 | Control Command Status: AUTO #0
63 | Control Command Status: AUTO #1
64 | Control Command Status: AUTO #2
65 | Control Command Status: Manual-Demo
66 | C.R. CORE# variation request: plus 1
67 | C.R. CORE# variation request: minus 1
68 | Failed CORE detection
69 | Eprom Checksum Fault
70 | Manual-Demo Control Command Pending
71 | Liebert communication fault
72 | DSAVE signal raised
73 | Cores number mismatch
74 | Battery Test not Allowed
75 | Battery Test Requested
76 | Battery Test Aborted or Failed
77 | Battery Test Cancelled
78 | Battery Test Not Possible
79 | Parallel Ups Number Mismatch
80 | Automatic Battery Test Not Enabled
81 | Manual Battery Test Not Enabled
82 | Common Battery Enabled
83 | Advanced Test Operating Mode
84 | Measures Data lost
85 | B.I.B. Communication Failed
100 | Ups fault
101 | System shutdown
102 | E.P.O. Active
103 | No start enabled
104 | Input air temperature out of range
105 | Input air temperature sensor fault
106 | Output air temperature out of range
107 | Output air temperature sensor fault
108 | Maintenance service recommended
109 | Ups OFF
110 | Ups wait to be synchronized
111 | Ups synchronized
112 | Ups stopped
113 | Inverter stopped by timer
114 | Inverter stopped by rs-232
115 | UPS temperature high
116 | Powerlan internal wiring fault
117 | Powerlan by-pass circuit failed closed
118 | Powerlan by-pass circuit failed open
119 | Powerlan PWM symmetry fault
120 | Powerlan IRQ hardware fault
121 | Powerlan hardware type fault
122 | Powerlan mains phase detector fault
123 | S1 preferred Line
124 | S2 preferred Line
125 | Manual Running
126 | Ups Warning
127 | Key Set to Bypass
128 | Reset fault key pressed
129 | Illegal software status
130 | Fan life exceeded
131 | Connection to charger lost
132 | Fiber Optic cable interface defective
133 | Temperature too high in device
134 | Incorrect power class configuration
135 | Failure power supply electronic
136 | DSP Program error
137 | Defect in power electronic (UCE supervision)
138 | False parameter input during H/W init
139 | CU EEPROM failure
140 | CU EEPROM failure check-sum error
141 | Environment temperature below zero / meas. defective
142 | CU Dual Port RAM access fault
143 | Parallel bypass failed during dynamic line support
144 | Parallel board signal failure
145 | Commissioning or test mode initiated
146 | CPU time slice override
147 | Warning 32
148 | Communication with battery manager defective
149 | Cross just started
150 | Cross switched off
151 | Manual commands enabled
152 | Controls override active
153 | Auxiliary power supply failure
154 | External command conflict
155 | Alarms latched (need to be reset by operator)
156 | Remote commands inhibited
157 | Mute key pressed
158 | Priority mode key pressed
159 | Transfer key pressed
160 | Priority mode (0 = FIXED, 1 = NO PRIORITY)
161 | Communication between CU and input converter lost
162 | Communication between CU and input converter failure
163 | Ventilation failure
164 | Cross 4 poles
165 | Cross Single phase
166 | Fan failure
167 | Vce Bridge fault ph R
168 | Vce Bridge fault ph S
169 | Vce Bridge fault ph T
170 | Generating set operation
171 | Forced synchronization
172 | Task Manager timeout
173 | Digital Interactive Mode Enable
174 | Keyboard locked
175 | High input air temperature
176 | Incorrect power class at start up
177 | Rectifier CU EEPROM failure
178 | Rectifier CU EEPROM failure check-sum error
179 | Rectifier auxiliary power supply failure
180 | Board not supplied
181 | Trace locked
182 | On board temperature out of range
183 | Not used
184 | On board temperature fault
185 | Ambient temperature out of range
186 | Ambient temperature above user settings
187 | Ambient temperature fault
197 | AC\DC desaturation phase U+ or U-
198 | AC\DC desaturation phase V+ or V-
199 | AC\DC desaturation phase W+ or W-
200 | Rectifier alarm
201 | Rectifier stage not valid
202 | Primary mains power failure
203 | Rectifier primary mains voltage outside limits
204 | Primary mains wrong phase rotation
205 | Mains frequency failure
206 | Input fuse blown
207 | Primary mains switch open
208 | Rectifier inhibit
209 | Rectifier blocked
210 | Generic rectifier fault
211 | Sw loss of dc reaction
212 | Sw loss of dc reaction (block)
213 | Hw loss of dc reaction
214 | Dc feedback fault
215 | Rectifier SCR fault
216 | Rectifier control fault
217 | Harmonic filter open
218 | Mains supporting boost
219 | Battery supplying boost
220 | Boost inhibited
221 | Boost blocked
222 | Boost over temperature
223 | Stop for boost over temperature
224 | Vdc out of Sw limits
225 | Vdc out of Hw limits
226 | Boost reference saturation
227 | Mains battery control fault
228 | Boost voltage low
229 | Boost unbalanced
230 | Battery charger running
231 | Battery charger in stand-by
232 | Battery charger failure
233 | Battery charger inhibit
234 | Battery charger blocked
235 | Mains voltage low
236 | Mains voltage high
237 | Rectifier positive control fault
238 | Rectifier negative control fault
239 | PFC soft start failure
240 | PFC rectifier failure
241 | KM1 switch failure
242 | Battery SCR control fault
243 | Primary Mains power recovered
244 | Charger stop switch
245 | Charger fuse blown
246 | High dc voltage
247 | Load circuit breaker open
248 | Low Dc Voltage
249 | Load Dc voltage high
250 | Load Dc voltage low
251 | Charger running
252 | Floating mode
253 | Charge mode
254 | Boost mode
255 | Minor charger fault
256 | Major charger fault
257 | Rectifier off
258 | Rectifier turning on
259 | Rectifier on
260 | VDC min threshold failed
261 | VDC min booster threshold failed
262 | VDC min inverter threshold failed
263 | Charger failure (detected by charger itself)
264 | Charger failure (detected by CU4)
265 | DC Under voltage
266 | DC Over voltage
267 | DC Voltage measure failed
268 | Primary Mains insulation fault
269 | Primary Mains transformer protection fault
270 | Emergency primary mains failure
271 | PFC mode
272 | Repeated low DC voltage
273 | Rectifier fault
274 | Rectifier Over temperature
275 | Charger Fault
276 | Charger Warning
277 | Manual Equalization mode
278 | Automatic Equalization mode
279 | Manual Battery Test
280 | Automatic Battery test
281 | charger Initialization
282 | Charger Test mode
283 | Charger specific Warning 1
284 | Charger specific Warning 2
285 | Charger specific Warning 3
286 | Charger specific fault 1
287 | Charger specific fault 2
288 | Charger specific fault 3
289 | Overload charger
290 | Rectifier filter over-temperature
291 | Rectifier over temperature warning
292 | Rectifier temperature sensor fault
293 | Rectifier contactor defective
294 | Boost/Charger filter over temperature
295 | Boost/Charger Over temperature
296 | Boost/Charger desaturation
297 | Boost/Charger temperature Fault
298 | Rectifier over temperature warning
299 | Charger high DC voltage
300 | Battery alarm
301 | Battery switch open
302 | Battery insulation failure
303 | Battery disconnected
304 | Battery SCR faulty
305 | Voltage probe faulty
306 | Flat battery
307 | Battery in top up
308 | Battery discharging
309 | Battery Shutdown Imminent
310 | Battery recharging
311 | Max battery recharging time exceeded
312 | Battery test
313 | Battery autonomy test
314 | Battery fault
315 | High battery temperature
316 | Battery temperature out of range
317 | Battery temperature probe not responding
318 | Battery lifetime exceeded
319 | Battery voltage low
320 | Battery voltage high
321 | Battery protection open
322 | Battery charger high
323 | Dc earth fault
324 | Battery contactor open
325 | Battery normal
326 | End of discharge
327 | Minor battery fault
328 | Major battery fault
329 | Imminent end battery autonomy time
330 | Battery completely discharged
331 | Battery gassing current too high
332 | Battery temperature fault
333 | Battery measurement module defective
334 | Internal battery resistance too high
335 | Poor battery voltage distribution
336 | Battery management not possible at this time
337 | Battery self discharge too high
338 | Battery capacity too small
339 | Battery conditioning recommended
340 | Battery circuit test recommended
341 | Incorrect battery load factor
342 | Connection to BAC lost
343 | BAC over temperature
344 | Commissioning BAC operating state
345 | Internal fault 71 (BAC)
346 | False BAC MLFB
347 | BAC inductor over current
348 | BAC UCE intermediate circuit
349 | BAC UCE battery side
350 | BAC over voltage in the intermediate circuit
351 | BAC over voltage in the battery circuit
352 | Cannot turn off the thyristor
353 | Battery fan feedback failure
354 | Optical cable failure
355 | BAC controller failure
356 | BAC current/voltage controller failure
357 | BAC controller overflow
358 | BAC thyristor failed
359 | BAC incorrect parameter entry
360 | Cannot turn off the thyristor (BAC off)
361 | BAC eeprom electronic defective
362 | BAC option module defective or not connect
363 | Battery fuse blown
364 | Battery thyristor failure
365 | Battery warning
366 | Battery specific Warning 1
367 | Battery specific Warning 2
368 | Battery specific Warning 3
369 | High DC Voltage memorized
370 | Battery current limit
371 | Remote switch off
372 | Input protection
374 | Battery specific Fault 1
375 | Battery specific Fault 2
376 | Battery specific Fault 3
377 | Battery start of discharging
378 | Battery test fault
379 | BMS warning
380 | Battery SCR temperature sensor fault
381 | Battery SCR over temperature
382 | Battery reverse connected
383 | Battery voltage over trace thershold
384 | Battery voltage under trace thershold
385 | Battery neg.pole insulation fault
386 | Battery pos.pole insulation fault
387 | Battery Idle
388 | External Battery Breaker Open
400 | Inverter alarm
401 | Inverter insufficient ventilation
402 | Inverter overload operation
403 | Stop due to over voltage or under voltage
404 | DC\AC desaturation phase U+ or U-
405 | DC\AC desaturation phase V+ or V-
406 | DC\AC desaturation phase W+ or W-
407 | Stop due to current limit
408 | Inhibited due to overload timeout
409 | Inhibited due to over temperature
410 | Inhibited due to max. dc voltage
411 | Inhibited due to min. dc voltage
412 | Inverter loss of phase lock
413 | Inverter stopped manually
414 | Inverter running
415 | Inverter off
416 | Inverter inhibited
417 | Inverter blocked
418 | Desaturation
419 | Over temperature
420 | Bypass output breaker closed
421 | Inverter voltage high
422 | Inverter voltage low
423 | Current limit
424 | Inverter static switch fault
425 | Inverter fail
426 | Bypass override
427 | PCB supply fault
428 | loss of inverter reaction
429 | inverter frequency below 1 percent
430 | inverter frequency out of limits
431 | Heat sink temperature fault
432 | Dc voltage to inverter high
433 | Dc voltage to inverter low
434 | Inv. stopped due to over voltage
435 | Inv. stopped due to under voltage
436 | Inverter fault
437 | High frequency
438 | Low frequency
439 | Overheating
440 | Inv. out of limits (1st level)
441 | Inv. out of limits (2nd level)
442 | Inverter static switch faulty
443 | Static switch blocked on inverter
444 | Inverter fuse blown
445 | Inverter static switch in short circuit
446 | Synchronized to crystal
447 | Inverter turning on
448 | Inverter on
449 | Inverter turning off
450 | Inverter over temperature warning
451 | Inverter over temperature fault
452 | Over temperature ph R
453 | Over temperature ph T
454 | Over temperature ph R,T
455 | Over temperature ph S
456 | Over temperatures ph R,S
457 | Over temperature ph T,S
458 | Over temperature ph R,S,T
459 | CPU program error
460 | Inverter contactor defective
461 | Multiple inverter cutoff for over current
462 | Over current cutoff
463 | Inverter remotely stopped
464 | Inverter output filter fault
465 | Inverter soft start failure
466 | Heat sink temperature out of range
467 | Inverter switched on
468 | Inverter fault from zsw2
469 | Inverter Warning
470 | Inverter synchronized
471 | Parallel off order
472 | Parallel operation
473 | Inverter overload warning
474 | Inverter overload fault
475 | Inverter User warning 1
476 | Inverter User warning 2
477 | Inverter User warning 3
478 | Inverter User fault 1
479 | Inverter User fault 2
480 | Inverter User fault 3
481 | Inverter filter over temperature
482 | Inverter over temperature sensor fault
483 | test
484 | Inverter supplied by rectifier
485 | Inverter supplied by battery
486 | Inverter not synchronized to automatic bypass
487 | Inverter not synchronized to external source
488 | Core "Sleep Command" active
489 | Trinergy Mode enabled
490 | Circular Redundancy enabled
491 | VFI Mode (Double Conversion)
492 | VI Mode (Line Interactive)
493 | VFD Mode (Stand-by)
494 | Generic Command pending
495 | Line Interactive Command pending
496 | Stand-by Command pending
497 | C.R. Mode (Circular Redundancy)
498 | Inverter voltage fault
499 | DC Bus not compatible with Batt.Voltage / Chg.Principle
500 | Reserve valid
501 | Reserve alarm
502 | Reserve input switch open
503 | Reserve stage not valid
504 | Reserve mains not valid
505 | Reserve inhibited
506 | Reserve fault
507 | Reserve high voltage
508 | Reserve low voltage
509 | Reserve high frequency
510 | Reserve low frequency
511 | Reserve mains wrong phase rotation
512 | Reserve mains voltage outside limits
513 | Reserve mains frequency outside limits
514 | Reserve mains slew rate outside limits
515 | Back feed protection active
516 | Reserve overload operation
517 | Reserve static switch blocked
518 | Reserve static switch in manual mode
519 | Static switch blocked on reserve
520 | Reserve static switch fault
521 | Reserve out of limits (1st level)
522 | Reserve out of limits (2nd level)
523 | Reserve static switch in short circuit
524 | Static switched to S1
525 | Static switched to S2
526 | S1 Voltage outside limits
527 | S1 Frequency outside limits
528 | S1 static switch in short circuit
529 | S1 static switch fault (open)
530 | S1 breaker open
531 | S1 bypass closed
532 | S2 Voltage outside limits
533 | S2 Frequency outside limits
534 | S2 static switch in short circuit
535 | S2 static switch fault (open)
536 | S2 breaker open
537 | S2 bypass closed
538 | Transfer inhibited for over current
539 | Manual transfer
540 | Bypass mains failure
541 | Bypass not installed
542 | Bypass on
543 | Bypass off
544 | Bypass fault
545 | Transfer to bypass inhibited
546 | Bypass overload timeout
547 | Bypass ph U fault
548 | Bypass ph V fault
549 | Bypass ph W fault
550 | Bypass several ph fault
551 | Bypass ready signal failure
552 | Bypass mains defective during dynamic line support
553 | Source selector switch
554 | External preferred source fail
555 | External reserve source fail
556 | Reserve transformer protection failure
557 | Reserve fuse blown
558 | S1 voltage in fatal state
559 | S1 voltage in critical state
560 | S1 frequency in fatal state
561 | S1 frequency in critical state
562 | S1 overheating
563 | S1 tripping coil active
564 | S2 voltage in fatal state
565 | S2 voltage in critical state
566 | S2 frequency in fatal state
567 | S2 frequency in critical state
568 | S2 overheating
569 | S2 tripping coil active
570 | Transfer inhibited
571 | External transfer inhibited
572 | Emergency reserve supply failure
573 | S1 neutral static switch in short circuit
574 | S2 neutral static switch in short circuit
575 | S1 neutral static switch fault (open)
576 | S2 neutral static switch fault (open)
577 | S1 neutral overheating
578 | S2 neutral overheating
579 | Bypass static switch fault / meas. defective
580 | S1 neutral over current
581 | S2 neutral over current
582 | Reserve Warning
583 | CIS parallel Fault
584 | Reserve static switch not correctly closed
585 | Reserve User warning 1
586 | Reserve User warning 2
587 | Reserve User warning 3
588 | Reserve User fault 1
589 | Reserve User fault 2
590 | Reserve User fault 3
591 | Reserve fault from zsw2
592 | Bypass input switch open
593 | Bypass mains power failure
594 | Bypass overload operation
595 | Bypass mains wrong phase rotation
596 | Emergency bypass mains failure (NO SMS)
597 | Bypass over temperature
598 | Bypass temperature fault
599 | Bypass over temperature fault
600 | Load alarm
601 | Output switch open
602 | Maintenance Bypass switch closed
603 | Load on direct line
604 | Load on conditioned line
605 | Output load supplied by reserve
606 | Output load supplied through maintenance bypass
607 | Output load not supplied
608 | Load on low priority line
609 | Load warning
610 | Static switch fail
611 | Overload
612 | Output threshold current
613 | Load current ph1 over 85%
614 | Load current ph2 over 85%
615 | Load current ph3 over 85%
616 | Dc component present
617 | Inverter static switch open
618 | Reserve static switch open
619 | Controlled line priority
620 | Direct line priority
621 | Output load supplied by battery
622 | Output voltage not calibrated
623 | Output transformer over temperature
624 | Output short circuit
625 | Load on inverter
626 | Output Voltage outside limits
627 | Maintenance Bypass switch closed
628 | Overload Warning (i2t Supervision)
629 | Overload Warning
630 | Overload Failure
631 | I2t ph R
632 | I2t ph S
633 | I2t ph T
634 | 90% overload capacity threshold reached
635 | Output out of tolerance
636 | Output over voltage
637 | Output under voltage
638 | Dc component present ph 1
639 | Dc component present ph 2
640 | Dc component present ph 3
641 | Output Frequency outside limits
642 | Output general fail
643 | Load on bad source
644 | End of overload timeout
645 | Output insulation failure
646 | Output load supplied by maintenance Bypass
647 | Load on bypass warning
648 | Static switch and ac load warning
649 | Static switch and ac load fault
650 | Static switch overload warning
651 | Static switch overload fault
652 | Output User warning 1
653 | Output User warning 2
654 | Output User warning 3
655 | Output User fault 1
656 | Output User fault 2
657 | Output User fault 3
658 | AC earth fault
659 | Output load supplied by bypass
660 | Output load supplied by inverter
661 | Load supplied
662 | Load frequency high
663 | Load frequency low
664 | High voltage THD
665 | High current THD
666 | Bypass filter over-temperature
667 | All Parallel Bypass are OK
668 | All Parallel Bypass are faulty
669 | One Parallel Bypass is faulty
670 | One(or more) Parallel Bypass is OK
671 | Output waveform error
672 | Bypass Input Fuse blown
700 | Reference frequency error
701 | Parallel ups offline
702 | Out of synchrony or cable not connected
703 | Ups self disconnection
704 | SBS output switch open
705 | SBS bypass switch closed
706 | Transmitted ITL signal
707 | Transmitted RTL signal
708 | Received ITL signal
709 | Received RTL signal
750 | Neutral Boost Filter Over temperature
751 | Neutral Boost over temperature
752 | Neutral Boost desaturation
753 | Neutral Boost temperature sensor fault
754 | Neutral Booster stabilizer over temperature warning
755 | Neutral switch open
756 | Precharge active
757 | Bypass disable for DC voltage low
758 | Precharge failure
759 | Precharge short circuit
760 | Precharge contactor feedback
761 Precharge in progress (50 Hz)
762 Precharge in progress
763 Walk-in in progress
764 Precharge in progress (60 Hz)
765 Neutral Boost Fault
766 Mains Voltage High Peak Detector
767 Rectifier Current Limit
768 Precharge Low UDC
769 Rectifier Overtemperature Fault
770 Rectifier Desaturation Fault
771 Rectifier stopped for overcurrent
775 Battery switch closure is inhibited
776 Ambient temperature probe not responding
777 Startup Synchronisation Error
778 | Neutral Boost over temperature warning
785 Charger Input Voltage High
786 Boost/Charger Overcurrent
787 Boost/Charger Overtemperature Warning
788 Boost/Charger temperature sensor fault
789 Boost/Charger Battery Measure fault
795 Bypass temperature sensor fault
796 | Booster Input Voltage High
797 | Charger off due to battery over-voltage
798 | Rectifier Desaturation (interrupt detection)
799 | Rectifier Desaturation (generic detection)
800 | C.O.C. failed
801 | Parallel not in synchrony
802 | Full load not available
803 | UPS 1 not supplied
804 | UPS 1 output breaker open
805 | UPS 1 voltage outside limits
806 | UPS 1 current limit
807 | UPS 2 not supplied
808 | UPS 2 output breaker open
809 | UPS 2 voltage outside limits
810 | UPS 2 current limit
811 | UPS 3 not supplied
812 | UPS 3 output breaker open
813 | UPS 3 voltage outside limits
814 | UPS 3 current limit
815 | UPS 4 not supplied
816 | UPS 4 output breaker open
817 | UPS 4 voltage outside limits
818 | UPS 4 current limit
819 | UPS 5 not supplied
820 | UPS 5 output breaker open
821 | UPS 5 voltage outside limits
822 | UPS 5 current limit
823 | UPS 6 not supplied
824 | UPS 6 output breaker open
825 | UPS 6 voltage outside limits
826 | UPS 6 current limit
827 | Reserve static switch over temperature
828 | Par reserve mains slew rate outside limits
829 | Par load alarm
830 | Par output breaker open
831 | Backup battery fault
832 | Diagnostic fault
833 | Ups not available
834 | Ups out of synchrony
835 | Ups current limit
836 | Ups voltage high
837 | Ups voltage low
838 | Ups 1 in alarm
839 | Ups 2 in alarm
840 | Ups 3 in alarm
841 | Ups 4 in alarm
842 | Ups 5 in alarm
843 | Ups 6 in alarm
844 | Insufficient Ups number
845 | Static switch blocked on Ups
846 | Output frequency out of limits
847 | Output insulation fault
848 | Heat sink over temperature
849 | Bypass transformer protection fault
850 | Loss of synchronism
851 | Parallel Bypass not available
852 | Inverter start pending command
853 | Inverter stop pending command
854 | Parallel On/Off problem
855 | Inverter start/stop pending command
856 | Inverter parallel error
857 | Battery Test Start pending command
858 | Battery Test Stop pending command
900 | IIC bus error
901 | Micro board I2C error
902 | Boost board I2C error
903 | Inverter board I2C error
904 | Non volatile memory error
905 | Not calibrated primary alarm
906 | Not calibrated secondary alarm
907 | Micro board not calibrated
908 | Display board revision warning
909 | Display board revision fatal
910 | Eeprom lost
911 | Eeprom revision warning
912 | Eeprom revision fatal
913 | Setup Data not initialized
914 | Cmos retention lost
915 | Cmos not initialized
916 | Timekeeper retention lost
917 | Timekeeper not initialized
918 | Eeprom lost (2nd I2C board)
919 | Eeprom revision warning (2nd I2C board)
920 | Eeprom revision fatal (2nd I2C board)
921 | Boost board not calibrated
922 | Inverter board not calibrated
923 | Setup data lost
924 | Bad area on micro board eeprom
925 | Battery charger not calibrated
930 | Solar application Profibus fault
931 | Solar application system frequency out of tolerance
932 | Solar application system voltage out of tolerance
933 | Warning 17
934 | Warning 18
935 | Warning 19
936 | Warning 20
937 | Warning 21
938 | Warning 22
939 | Warning 25
940 | Warning 26
941 | Warning 27
942 | Warning 28
943 | Warning 29
944 | Warning 30
945 | Warning 31
946 | Fault 48
947 | Fault 49
948 | Fault 53
949 | Fault 54
950 | Fault 56
951 | Fault 62
952 | Fault 63
953 | Fault 64
954 | Fault 65
955 | Fault 66
956 | Fault 67
957 | Fault 68
958 | Fault 69
959 | Fault 70
960 | Fault 71
961 | Fault 72
962 | Fault 73
963 | Fault 74
964 | Fault 75
965 | Fault 76
966 | Fault 77
967 | Fault 78
968 | Primary mains input sensor fault
969 | Fault 80
970 | Fault 81
971 | Fault 82
972 | Fault 83
973 | Fault 84
974 | Fault 85
975 | Fault 86
976 | Fault 87
977 | Fault 88
978 | Fault 89
979 | Fault 90
980 | Fault 91
981 | Fault 92
982 | Fault 93
983 | Fault 94
984 | Fault 95
985 | Fault 96
986 | Fault 97
987 | Fault 98
988 | Fault 99
989 | Reserved event 6
990 | Negative Adjust time
991 | Display control board memory fault
1000 | Synchronization system fault
1001 | Synchronization communication fault
1002 | Synchronization system active
1003 | Synchronization system inactive
1004 | Synchronization system inhibited
1005 | Synchronization to mains inhibited
1006 | Simultaneous fault in Boost/Charger and Rectifier
1100 | Control set to stop
1101 | Control set to automatic
1102 | Control set to manual
1103 | Control set to test on load
1104 | Control set to manual restore
1105 | D S Module front panel editor in operation
1106 | Warning Alarm active
1107 | Electrical Trip Alarm active
1108 | Shutdown Alarm active
1109 | Deep Sea control module failed
1110 | Deep Sea control module not configured
1111 | Emergency stop operated
1112 | Low oil pressure
1113 | High coolant temperature
1114 | High oil temperature
1115 | Engine underspeed
1116 | Engine overspeed
1117 | Engine failed to start
1118 | Engine failed to stop
1119 | Loss of speed signal (MPU)
1120 | Generator low voltage
1121 | Generator high voltage
1122 | Generator low frequency
1123 | Generator high frequency
1124 | Generator high current
1125 | Generator earth fault
1126 | Generator reverse power
1127 | Air flap(s) operated (overspeed)
1128 | Oil pressure sender fault
1129 | Coolant temperature sender fault
1130 | Oil temperature sender fault
1131 | Fuel level sender fault
1132 | Magnetic pickup fault
1133 | Loss of speed signal (AC)
1134 | Charge alternator failed
1135 | Plant battery low voltage
1136 | Plant battery high voltage
1137 | Day tank fuel level low
1138 | Day tank fuel level high
1139 | Generator breaker/contactor fail to close
1140 | Mains breaker/contactor fail to close
1141 | Generator breaker/contactor fail to open
1142 | Mains breaker/contactor fail to open
1143 | Mains supply voltage low
1144 | Mains supply voltage high
1145 | Bus breaker/contactor fail to close
1146 | Bus breaker/contactor fail to open
1147 | Mains supply frequency low
1148 | Mains supply frequency high
1149 | Mains supply failed
1150 | Mains supply phase sequence wrong
1151 | Generator supply phase sequence wrong
1152 | Maintenance Due
1153 | Clock Not Set
1154 | D S module language and contrast setting lost
1155 | D S module communications settings lost
1156 | Modem Power Fail
1157 | Generator short circuit
1158 | Generator failed to synchronize
1159 | Bus live
1160 | Scheduled Run
1161 | Bus Phase Rotation Wrong
1162 | D S module Gen' set run priority selection error
1163 | Multiset comm's link data transfer error
1164 | Share violation of mulitset ID
1165 | Multiset comm's data link complete failure
1166 | Multiset comm's too few sets per configuration
1167 | Multiset comm's link failure
1168 | Multiset old version
1169 | Mains reverse power
1170 | Minimum amount of muliple sets not reached
1171 | Insufficent capacity avialable
1172 | Expansion input unit not calibrated
1173 | Expansion input unit failed
1174 | Ambient room temperature low
1175 | Ambient room temperature high
1176 | Ambient room temperature fault
1177 | Bulk tank fuel level low
1178 | Bulk tank fuel level high
1179 | Bulk tank fuel level fault
1180 | Engine ECU CAN bus lost
1181 | Engine ECU CAN bus failed
1182 | Engine ECU CAN bus error
1183 | Low coolant temperature
1184 | Voltage phase slip after breaker command
1185 | Generator room door open
1186 | Generator room access authourised
1187 | Engine heater or Battery charger off
1188 | Warning alarm active (Main panel)
1189 | Maintenace in progress
1190 | Generator Set local breaker open
1191 | Remote Start
1192 | Manual Mode (Main panel)
1193 | Emergency Stop (Main panel)
1194 | Shutdown active (Main panel)
1195 | Expansion input 5
1196 | Expansion input 6
1197 | Auto Mode (Main panel)
1198 | Stop mode (Main panel)
1199 | Digital Output 1 (Module 1)
1200 | Digital Output 2 (Module 2)
1201 | Digital Output 3 (Module 3)
1202 | Digital Output 4 (Module 4)
1203 | Digital Output 5 (Module 5)
1204 | Digital Output 6 (Module 6)
1205 | A1 digital expansion output
1206 | A2 digital expansion output
1207 | A3 digital expansion output
1208 | A4 digital expansion output
1209 | A5 Digital expansion output
1210 | A6 digital expansion output
1211 | A7 digital expansion output
1212 | A8 digital expansion output
1213 | B1 digital expansion output
1214 | B2 digital expansion output
1215 | B3 digital expansion output
1216 | B4 digital expansion output
1217 | B5 digital expansion output
1218 | Mains on load
1219 | Generator on load
1220 | Generator Runnning
1221 | DSE5320 - Shadow unit
1230 | Current limit pre-alarm
1231 | Current limit alarm
1232 | Current limit (phase 1) over threshold 1 pre-alarm
1233 | Current limit (phase 1) over threshold 1 alarm
1234 | Current limit (phase 1) over threshold 2 pre-alarm
1235 | Current limit (phase 1) over threshold 2 alarm
1236 | Current limit (phase 1) over threshold 3 pre-alarm
1237 | Current limit (phase 1) over threshold 3 alarm
1238 | Current limit (phase 1) over threshold 4 pre-alarm
1239 | Current limit (phase 1) over threshold 4 alarm
1240 | Current limit (phase 2) over threshold 1 pre-alarm
1241 | Current limit (phase 2) over threshold 1 alarm
1242 | Current limit (phase 2) over threshold 2 pre-alarm
1243 | Current limit (phase 2) over threshold 2 alarm
1244 | Current limit (phase 2) over threshold 3 pre-alarm
1245 | Current limit (phase 2) over threshold 3 alarm
1246 | Current limit (phase 2) over threshold 4 pre-alarm
1247 | Current limit (phase 2) over threshold 4 alarm
1248 | Current limit (phase 3) over threshold 1 pre-alarm
1249 | Current limit (phase 3) over threshold 1 alarm
1250 | Current limit (phase 3) over threshold 2 pre-alarm
1251 | Current limit (phase 3) over threshold 2 alarm
1252 | Current limit (phase 3) over threshold 3 pre-alarm
1253 | Current limit (phase 3) over threshold 3 alarm
1254 | Current limit (phase 3) over threshold 4 pre-alarm
1255 | Current limit (phase 3) over threshold 4 alarm
1256 | Load voltage low quality
1257 | Load voltage low quality (phase 1) over threshold 1
1258 | Load voltage low quality (phase 1) over threshold 2
1259 | Load voltage low quality (phase 1) over threshold 3
1260 | Load voltage low quality (phase 1) over threshold 4
1261 | Load voltage low quality (phase 1) under threshold 1
1262 | Load voltage low quality (phase 1) under threshold 2
1263 | Load voltage low quality (phase 1) under threshold 3
1264 | Load voltage low quality (phase 1) under threshold 4
1265 | Load voltage low quality (phase 2) over threshold 1
1266 | Load voltage low quality (phase 2) over threshold 2
1267 | Load voltage low quality (phase 2) over threshold 3
1268 | Load voltage low quality (phase 2) over threshold 4
1269 | Load voltage low quality (phase 2) under threshold 1
1270 | Load voltage low quality (phase 2) under threshold 2
1271 | Load voltage low quality (phase 2) under threshold 3
1272 | Load voltage low quality (phase 2) under threshold 4
1273 | Load voltage low quality (phase 3) over threshold 1
1274 | Load voltage low quality (phase 3) over threshold 2
1275 | Load voltage low quality (phase 3) over threshold 3
1276 | Load voltage low quality (phase 3) over threshold 4
1277 | Load voltage low quality (phase 3) under threshold 1
1278 | Load voltage low quality (phase 3) under threshold 2
1279 | Load voltage low quality (phase 3) under threshold 3
1280 | Load voltage low quality (phase 3) under threshold 4
1281 | Load over voltage pre-alarm
1282 | Load over voltage alarm
1283 | Load over voltage (phase 1) over threshold 1 pre-alarm
1284 | Load over voltage (phase 1) over threshold 1 alarm
1285 | Load over voltage (phase 1) over threshold 2 pre-alarm
1286 | Load over voltage (phase 1) over threshold 2 alarm
1287 | Load over voltage (phase 1) over threshold 3 pre-alarm
1288 | Load over voltage (phase 1) over threshold 3 alarm
1289 | Load over voltage (phase 1) over threshold 4 pre-alarm
1290 | Load over voltage (phase 1) over threshold 4 alarm
1291 | Load over voltage (phase 2) over threshold 1 pre-alarm
1292 | Load over voltage (phase 2) over threshold 1 alarm
1293 | Load over voltage (phase 2) over threshold 2 pre-alarm
1294 | Load over voltage (phase 2) over threshold 2 alarm
1295 | Load over voltage (phase 2) over threshold 3 pre-alarm
1296 | Load over voltage (phase 2) over threshold 3 alarm
1297 | Load over voltage (phase 2) over threshold 4 pre-alarm
1298 | Load over voltage (phase 2) over threshold 4 alarm
1299 | Load over voltage (phase 3) over threshold 1 pre-alarm
1300 | Load over voltage (phase 3) over threshold 1 alarm
1301 | Load over voltage (phase 3) over threshold 2 pre-alarm
1302 | Load over voltage (phase 3) over threshold 2 alarm
1303 | Load over voltage (phase 3) over threshold 3 pre-alarm
1304 | Load over voltage (phase 3) over threshold 3 alarm
1305 | Load over voltage (phase 3) over threshold 4 pre-alarm
1306 | Load over voltage (phase 3) over threshold 4 alarm
1307 | Load under voltage pre-alarm
1308 | Load under voltage alarm
1309 | Load under voltage (phase 1) under threshold 1 pre-alarm
1310 | Load under voltage (phase 1) under threshold 1 alarm
1311 | Load under voltage (phase 1) under threshold 2 pre-alarm
1312 | Load under voltage (phase 1) under threshold 2 alarm
1313 | Load under voltage (phase 1) under threshold 3 pre-alarm
1314 | Load under voltage (phase 1) under threshold 3 alarm
1315 | Load under voltage (phase 2) under threshold 1 pre-alarm
1316 | Load under voltage (phase 2) under threshold 1 alarm
1317 | Load under voltage (phase 2) under threshold 2 pre-alarm
1318 | Load under voltage (phase 2) under threshold 2 alarm
1319 | Load under voltage (phase 2) under threshold 3 pre-alarm
1320 | Load under voltage (phase 2) under threshold 3 alarm
1321 | Load under voltage (phase 3) under threshold 1 pre-alarm
1322 | Load under voltage (phase 3) under threshold 1 alarm
1323 | Load under voltage (phase 3) under threshold 2 pre-alarm
1324 | Load under voltage (phase 3) under threshold 2 alarm
1325 | Load under voltage (phase 3) under threshold 3 pre-alarm
1326 | Load under voltage (phase 3) under threshold 3 alarm
1327 | Battery low (Digital input)
1328 | Load on automatic by-pass (Digital input)
1329 | Primary mains failure (Digital input)
1330 | Load supplied (Digital input)
1331 | Digital input 1
1332 | Digital input 2
1333 | Digital input 3
1334 | Digital input 4
1335 | Digital input 5
1336 | Digital input 6
1337 | Digital input 7
1338 | Digital input 8
1339 | On board battery on charge
1340 | On board battery fault
1341 | On board battery ready
1342 | Generator running (Digital input)
1343 | Common fault (Digital input)
1344 | Day tank fuel level low (Digital input)
1345 | Bulk tank fuel level fault (Digital input)
1346 | Auto mode (Digital input)
1347 | Mains on load (Digital input)
1348 | Generator on load (Digital input)
1349 | Battery fault
1350 | High coolant temperature
1351 | Low coolant temperature
1352 | emergency stop (Digital input)
1353 | Mains available
1354 | Generator available
1355 | Generator room door open (Digital input)
1400 | External inhibit
1401 | Mains abnormal
1402 | Phase 1 CT F/B Wrong
1403 | Phase 2 CT F/B Wrong
1404 | Phase 3 CT F/B Wrong
1405 | Fast DC Over Voltage
1406 | Over Current
1407 | Filter trip
1408 | Filter Off
1409 | Boost charge timeout
1410 | Display error
1500 | General Stage Fault
1501 | Shutdown Command Pending
1502 | D.I.C. Power-Up
1503 | Id Card Missing
1504 | D.I.C. Software Error
1505 | D.I.C. Hardware Failure
1506 | I2C (I/O Expander) Init Failed
1507 | I2C Multiple Error I/O Expander
1508 | I2C Multiple Error ID Card
1509 | Parallel Cable Fitted Signal Is Missing
1510 | Rectifier Warning
1511 | Rectfier Hardware Failure
1512 | Battery Conditioning Active
1513 | Manual Battery Test Recommended
1514 | Charger Is Switched Off
1515 | Charger Manual Running
1516 | Charger Off due to a failure
1517 | Charger Measure Feedback Error
1518 | Charger Warning Due To Input Voltage Low
1519 | Charger Output Short Circuit Detected
1520 | Charger Off Due To Output Short Circuit Deetected
1521 | No Battery Detected
1522 | Charger Output Short Circuit Detected while Forced ON
1523 | Charger Reverse Polarity Detected
1524 | Charger Communication Not Possible
1525 | Booster Off
1526 | Booster Turning On
1527 | Booster On
1528 | Booster Stop Due To Fault
1529 | Booster Fault
1530 | Booster Warning
1531 | Booster Overcurrent
1532 | Source Of Synchronization Is Bypass
1533 | Source Of Synchronization Is Output
1534 | Source Of Synchronization Is Self Clock (internal)
1535 | Source Of Synchronization Is External
1536 | Bypass Warning
1537 | Bypass With Delay
1538 | Reserved Event 3
1539 | Reserved Event 4
1540 | D.I.C. Summary Warning
1541 | D.I.C. Summary Fault
1542 | Bypass Hardware Failure
1543 | Rectifier Overload
1544 | Rect. Self Test fail Ph U positive
1545 | Rect. Self Test fail Ph U negative
1546 | Rect. Self Test fail Ph V positive
1547 | Rect. Self Test fail Ph V negative
1548 | Rect. Self Test fail Ph W positive
1549 | Rect. Self Test fail Ph W negative
1550 | Inverter Self Test fail Ph U positive
1551 | Inverter Self Test fail Ph U negative
1552 | Inverter Self Test fail Ph V positive
1553 | Inverter Self Test fail Ph V negative
1554 | Inverter Self Test fail Ph W positive
1555 | Inverter Self Test fail Ph W negative
1556 | Inverter under voltage - phase 1
1557 | Inverter under voltage - phase 2
1558 | Inverter under voltage - phase 3
1559 | Inverter over voltage - phase 1
1560 | Inverter over voltage - phase 2
1561 | Inverter over voltage - phase 3
1562 | Inverter temperature fault
1563 | Battery Grounding Error
1564 | Wound component OT
1565 | Semiconductor OT
1566 | Rectifier driver fault
1567 | Inverter driver fault
1568 | DC fuse fail
1569 | DC offset high
1570 | Forced transfer to bypass
1571 | Load on Battery
1572 | Load on manual bypass
1573 | Battery voltage low alarm
1574 | SPI communication fail
1575 | Emergency load on bypass
1576 | Rectifier Over Voltage
1577 | Inverter fuse blown phase U
1578 | Inverter fuse blown phase V
1579 | Inverter fuse blown phase W
1580 | Inverter Desaturation (interrupt detection)
1581 | Inverter Desaturation (generic detection)
1600 | One or more fuses blown
1601 | UPS off line mode
1602 | Module 1 summary event
1603 | Module 2 summary event
1604 | Module 3 summary event
1605 | Module 4 summary event
1606 | Module PFC not installed
1607 | Module Charger not installed
1608 | Module Inverter not installed
1609 | Module not powered
1610 | Module fault shutdown
1611 | Module Charger circuit general fault
1612 | Module PFC fuse open fault
1613 | Module PFC over temperature warning
1614 | Module PFC over temperature shutdown
1615 | Module DC bus over voltage warning
1616 | Module DC bus under voltage warning
1617 | Module DC bus under voltage shutdown
1618 | Module PFC circuit general fault
1619 | Module Fan failure
1620 | Module Inner communication failure
1621 | Module Not calibrated
1622 | Module Inverter fuse open
1623 | Module Inverter over temperature warning
1624 | Module Inverter over temperature shutdown
1625 | Module Inverter short circuit
1626 | Module Inverter STS failure
1627 | Module Inverter voltage abnormal
1628 | Module Inverter circuit general fault shutdown
1629 | Module Inner communication loss
1630 | Module EPO shutdown
1631 | Module Inverter parallel communication loss
1632 | Module Inverter parallel failure
1633 | Module Not calibrated
1634 | UPS in stand-by
1635 | UPS loss of redundancy
1636 | Module 1 not filled
1637 | Module 2 not filled
1638 | Module 3 not filled
1639 | Module 4 not filled
1640 | Short circuit ph1-N
1641 | Short circuit ph2-N
1642 | Short circuit ph3-N
1643 | Short circuit ph1-ph2
1644 | Short circuit ph2-ph3
1645 | Short circuit ph3-ph1
1646 | Inverter relay open fault
1647 | Inverter relay close fault
1648 | Bypass SCR fault
1649 | PFC over current
1650 | CAN communication error
1651 | Bypass mode no operation
1652 | Parallel line loss
1653 | Battery wiring error
1654 | Battery maintenance recommended
1655 | Inform guarantee
1656 | UPS temperature low
1657 | Bus capacitors maintenance recommended
1658 | Internal warning
1659 | UPS board hasn't detected the UPS
1660 | Ups adapter connection lost
1661 | Rectifier startup failure
1662 | Rectifier fuse blown
1663 | Rectifier inductor over temperature
1664 | Dc bus balancer over temperature
1665 | dc bus balancer over current
1666 | dc bus balancer fault
1667 | dc bus #1 power supply fail
1668 | main neutral lost
1669 | Rectifier communication failure
1670 | Inverter ready
1671 | Inverter inductor overtemperature
1672 | Inverter communication failure
1673 | Bypass phase lost
1674 | Bypass transfer count block
1675 | Static bypass switch disabled
1676 | Output fuse blown
1677 | Overload transfer to bypass
1678 | Battery test passed
1679 | Battery test failed
1680 | Battery charge compensation active
1681 | Battery contactor fail
1682 | Battery converter over current
1683 | Battery converter fail
1684 | Battery converter over temperature
1685 | Parallel low battery warning
1686 | Load share fault
1687 | Parallel system fault
1688 | Parallel connector error
1689 | Parallel system overload
1690 | Parallel transfer to static bypass switch
1691 | Parallel communication fault
1692 | Operation fault
1693 | Generator disconnected
1694 | Parallel load source unknown
1695 | Parallel load on utility
1696 | Parallel load on battery
1697 | Parallel load source on bypass
1698 | Parallel load source no output
1699 | Rotary breaker status - unknown
1700 | Rotary breaker status - closed
1701 | Rotary breaker status - test
1702 | Rotary breaker status - normal
1703 | Rotary breaker status - bypass
1704 | Rotary breaker status - maintenance
1800 | S1 SCR Short
1801 | S2 SCR Short
1802 | S1 SCR Open
1803 | S2 SCR Open
1804 | Control Module Fail
1805 | PWR Supply DC A Fail
1806 | PWR Supply DC B Fail
1807 | PWR Supply SRC 1 AC Fail
1808 | PWR Supply SRC 2 AC Fail
1809 | PWR Supply Logic Fail
1810 | Output Voltage Sense Fail
1811 | S1 Voltage Sense Fail
1812 | S2 Voltage Sense Fail
1813 | S1 SCR Sense Fail
1814 | S2 SCR Sense Fail
1815 | S1 Current Sense Fail
1816 | S2 Current Sense Fail
1817 | S1 Gate Drive Fail
1818 | S2 Gate Drive Fail
1819 | Internal Comm Fail
1820 | External Comm Fail
1821 | CB1 Shunt Trip Fail
1822 | CB2 Shunt Trip Fail
1823 | S1 Overcurrent
1824 | S2 Overcurrent
1825 | S1 I Peak
1826 | S2 I Peak
1827 | Load On Alternate Source
1828 | CB3A Output Bkr Open
1829 | S1 Phase Rotation Error
1830 | S2 Phase Rotation Error
1831 | History Logs Full
1832 | Ground Over current
1833 | Neutral Over current
1834 | P4 Neutral Curr 1 Over Limit
1835 | P4 Neutral Curr 2 Over Limit
1836 | P4 Neutral Snubber Fail
1837 | P4 Neutral 1 SCR Short
1838 | P4 Neutral 2 SCR Short
1839 | P4 Neutral 1 SCR Open
1840 | P4 Neutral 2 SCR Open
1841 | Battery Equalize
1842 | System Input Power Problem
1843 | LBS Inhibited
1844 | MMS Overload
1845 | System Input Current Imbalance
1846 | Battery Not Qualified
1847 | Load Sharing Fault
1848 | DC Bus Abnormal
1849 | Load Impact Transfer
1850 | User Operation Invalid
1851 | Power Sub Module Fault
1852 | MMS On Battery
1853 | Bypass Backfeed
1854 | Bypass Sync Inhibited
1860 | Changed SN or type
1861 | Bypass Excessive Pulse Parallel
1862 | Bypass Auto Transfer Failed
1863 | Battery Charging Reduced-Extrnl
1864 | System Shutdown - REPO
1865 | System Output Low Power Factor
1866 | Input Contact 14
1867 | Input Contact 15
1868 | Input Contact 16
1869 | Auto Restart In Progress
1870 | Auto Restart Inhibited - Ext
1871 | Backfeed Breaker Open
1872 | Input Filter Cycle Lock
1873 | Parallel Bypass Retransfer Inhibit
1874 | Parallel Loss of Sync Pulse
1875 | ECO Mode Active
1876 | LBS Active - Master
1877 | LBS Active - Slave
1878 | EMO Shutdown
1879 | Parallel BypassTransfer Inhibit
1880 | Parallel Bypass Static Switch Start Inhibited
1881 | System Shutdown - Transformer Over Temperature
1882 | System Shutdown - Remote Shutdown
1883 | System Shutdown - Hardware Fault
1884 | Output power over 85% for one or more phase

## life_measures
0 | Mains Voltage
1 | Dc Voltage
2 | Dc Voltage (+)
3 | Dc Voltage (-)
4 | Dc Current
5 | Boost Current
6 | Battery Current
7 | Battery Voltage
8 | Reserve Voltage
9 | Reserve Voltage Ph1
10 | Reserve Voltage Ph2
11 | Reserve Voltage Ph3
12 | Reserve Frequency
13 | Inverter Voltage
14 | Inverter Voltage Ph1
15 | Inverter Voltage Ph2
16 | Inverter Voltage Ph3
17 | Inverter Current
18 | Inverter Frequency
19 | Output Voltage
20 | Output Voltage Ph1
21 | Output Voltage Ph2
22 | Output Voltage Ph3
23 | Output Frequency
24 | Load Current
25 | Load Current Ph1
26 | Load Current Ph2
27 | Load Current Ph3
28 | Load Percentage Ph1
29 | Load Percentage Ph2
30 | Load Percentage Ph3
31 | Overload Threshold
32 | Battery temperature
33 | Inlet Air temperature
34 | Outlet Air temperature
35 | Heat Sink temperature
36 | Mains Frequency
37 | S1 Voltage Ph1
38 | S1 Voltage Ph2
39 | S1 Voltage Ph3
40 | S2 Voltage Ph1
41 | S2 Voltage Ph2
42 | S2 Voltage Ph3
43 | S1 Frequency
44 | S2 Frequency
45 | S1 S2 Phase Error
46 | Dc Voltage i2c
47 | Inlet Air temperature 2
48 | Outlet Air temperature 2
49 | Mains Voltage Ph1
50 | Mains Voltage Ph2
51 | Mains Voltage Ph3
52 | Battery capacity
53 | Heat sink temperature Ph1
54 | Heat sink temperature Ph2
55 | Heat sink temperature Ph3
56 | Load real power Ph1
57 | Load real power Ph2
58 | Load real power Ph3
59 | Load apparent power Ph1
60 | Load apparent power Ph2
61 | Load apparent power Ph3
62 | Neutral output current
63 | Neutral S1-S2 Dv
64 | Oil pressure
65 | Coolant temperature
66 | Oil temperature
67 | Fuel level
68 | Charge alt voltage
69 | Battery voltage
70 | Engine speed
71 | Generator frequency
72 | Generator L1-N voltage
73 | Generator L2-N voltage
74 | Generator L3-N voltage
75 | Generator L1-L2 voltage
76 | Generator L2-L3 voltage
77 | Generator L3-L1 voltage
78 | Generator L1 current
79 | Generator L2 current
80 | Generator L3 current
81 | Generator earth current
82 | Generator L1 KW
83 | Generator L2 KW
84 | Generator L3 KW
85 | Generator current lag lead
86 | Mains frequency
87 | Mains L1-N voltage
88 | Mains L2-N voltage
89 | Mains L3-N voltage
90 | Mains L1-L2 voltage
91 | Mains L2-L3 voltage
92 | Mains L3-L1 voltage
93 | Generator total KW
94 | Generator L1 VA
95 | Generator L2 VA
96 | Generator L3 VA
97 | Generator total VA
98 | Generator L1 VAr
99 | Generator L2 VAr
100 | Generator L3 VAr
101 | Generator total VAr
102 | Generator power factor L1
103 | Generator power factor L2
104 | Generator power factor L3
105 | Generator average power factor
106 | Ambient temperature
107 | Bulk tank fuel level
108 | Battery Voltage pos
109 | Battery Voltage neg
110 | Battery PE skew
111 | Load apparent power
112 | Load real power
113 | Output Voltage THD
114 | Output Voltage THD Ph1
115 | Output Voltage THD Ph2
116 | Output Voltage THD Ph3
117 | Output Current THD
118 | Output Current THD Ph1
119 | Output Current THD Ph2
120 | Output Current THD Ph3
121 | On Board temperature
122 | Power Factor Ph1
123 | Power Factor Ph2
124 | Power Factor Ph3
125 | Mains Current Ph1
126 | Mains Current Ph2
127 | Mains Current Ph3
128 | Rectifier temperature Ph1
129 | Rectifier temperature Ph2
130 | Rectifier temperature Ph3
131 | Rectifier temp.ext. Ph1
132 | Rectifier temp.ext. Ph2
133 | Rectifier temp.ext. Ph3
134 | Heat sink temp.ext. Ph1
135 | Heat sink temp.ext. Ph2
136 | Heat sink temp.ext. Ph3
137 | Reserve temperature
138 | Reserve temp.ext.
139 | Boost temp.
140 | Boost ext./Boost 2 temp.
141 | Positive Battery voltage
142 | Positive Battery capacity
143 | Negative Battery voltage
144 | Negative Battery capacity
145 | Mains real power Ph1
146 | Mains real power Ph2
147 | Mains real power Ph3
148 | Mains apparent power Ph1
149 | Mains apparent power Ph2
150 | Mains apparent power Ph3
151 | Input power factor
152 | Reserve Current Ph1
153 | Reserve Current Ph2
154 | Reserve Current Ph3
155 | Reserve real power Ph1
156 | Reserve real power Ph2
157 | Reserve real power Ph3
158 | Output power factor
159 | Estimated battery Charge
160 | Positive Battery Current
161 | Negative Battery Current
162 | O/P load
163 | Battery time remaining
164 | Input power factor L1
165 | Input power factor L2
166 | Input power factor L3
167 | Output current crest factor L1
168 | Output current crest factor L2
169 | Output current crest factor L3
170 | Reserve total real power
171 | Reserve apparent power Ph1
172 | Reserve apparent power Ph2
173 | Reserve apparent power Ph3
174 | Reserve total apparent power
175 | Efficiency
176 | Total Loss
177 | Total Load Percentage
178 | Bypass Power Factor Ph1
179 | Bypass Power Factor Ph2
180 | Bypass Power Factor Ph3
181 | Bypass total Power Factor
182 | Boost 2/Boost 3 temp.
183 | Boost 2 ext./Boost 4 temp.
184 | Source 1 Current A
185 | Source 1 Current B
186 | Source 1 Current C
187 | Source 2 Current A
188 | Source 2 Current B
189 | Source 2 Current C
190 | P4 Source 1 Volts A N
191 | P4 Source 1 Volts B N
192 | P4 Source 1 Volts C N
193 | P4 Source 2 Volts A N
194 | P4 Source 2 Volts B N
195 | P4 Source 2 Volts C N
196 | P4 Source 1 Neutral Current
197 | P4 Source 2 Neutral Current
198 | System Output Voltage RMS A-B
199 | System Output Voltage RMS B-C
200 | System Output Voltage RMS C-A
201 | System Output Pct Power Phase A
202 | System Output Pct Power Phase B
203 | System Output Pct Power Phase C
204 | Parallel - Output Apparent Power
205 | Parallel - Output Power
206 | Reserve L1-L2 voltage
207 | Reserve L2-L3 voltage
208 | Reserve L3-L1 voltage
209 | Output L1-L2 voltage
210 | Output L2-L3 voltage
211 | Output L3-L1 voltage
212 | Battery Discharge Power
213 | System Output RMS Current Phs A
214 | System Output RMS Current Phs B
215 | System Output RMS Current Phs C
216 | System Output Power Factor Phs A
217 | System Output Power Factor Phs B
218 | System Output Power Factor Phs C
219 | Inverter Overload Time Remaining
220 | Parallel - Output Voltage RMS A-B
221 | Parallel - Output Voltage RMS B-C
222 | Parallel - Output Voltage RMS C-A
223 | Parallel - Sum of Output RMS Currents for Phase A
224 | Parallel - Sum of Output RMS Currents for Phase B
225 | Parallel - Sum of Output RMS Currents for Phase C
226 | Parallel - Output Frequency
227 | Parallel - Output Power Factor Phase A
228 | Parallel - Output Power Factor Phase B
229 | Parallel - Output Power Factor Phase C