## Events
IP= | 127.0.0.1 | Email | darryl.brown@emerson.com | SMTP server= | 10.16.67.249 | Enable= | y
PointId | Point Label | LifeId | life event | ORed event | EmerDelay | Event State | multi-module index | Optional Delay (sec) | EmerDelay y / n | Run y / n
4122 | System Input Power Problem | 202 | Primary mains power failure |  | Immediate | 19 | 0 | 0 | n | y
4132 | Bypass Overload Phase A | 594 | Bypass overload operation |  | 1 minute | 19 | 0 | 0 | n | y
4133 | Bypass Overload Phase B | 594 | Bypass overload operation |  | 1 minute | 19 | 0 | 0 | n | y
4134 | Bypass Overload Phase C | 594 | Bypass overload operation |  | 1 minute | 19 | 0 | 0 | n | y
4135 | Bypass Not Available | 593 | Bypass mains power failure |  | Immediate | 19 | 0 | 0 | n | y
4138 | Bypass Auto Retransfer Failed | 545 | Transfer to bypass inhibited |  |  | 19 | 0 | 0 | n | y
4139 | Bypass - Excess Auto Retransfers | 545 | Transfer to bypass inhibited |  |  | 19 | 0 | 0 | n | y
4142 | Bypass Static Switch Overload | 650 | Static switch overload warning |  | 10 minutes | 19 | 0 | 0 | n | y
4143 | Bypass Static Switch Unavailable | 579 | Bypass static switch fault / meas. defective |  |  | 19 | 0 | 0 | n | y
4144 | Bypass Excessive Pulse Parallel | 1861 | Bypass Excessive Pulse Parallel |  |  | 19 | 0 | 0 | n | y
4145 | Bypass Auto Transfer Failed | 1862 | Bypass Auto Transfer Failed |  |  | 19 | 0 | 0 | n | y
4146 | System Input Phs Rotation Error | 204 | Primary mains wrong phase rotation |  | 1 minute | 19 | 0 | 0 | n | y
4147 | System Input Current Limit | 423 | Current limit |  | 1 minute | 19 | 0 | 0 | n | y
4162 | Battery Low | 309 | Battery Shutdown Imminent |  | 10 minutes | 19 | 0 | 0 | n | y
4164 | Battery Charging Error | 232 | Battery charger failure |  | 10 minutes | 19 | 0 | 0 | n | y
4165 | Battery Charging Reduced-Extrnl | 1863 | Battery Charging Reduced-Extrnl |  |  | 19 | 0 | 0 | n | y
4166 | Battery Capacity Low | 338 | Battery capacity too small | X | 1 minute | 19 | 0 | 0 | n | y
4168 | Battery Discharging | 308 | Battery discharging | X |  | 19 | 0 | 0 | n | y
4169 | Battery Temperature Imbalance | 315 | High battery temperature | X | 1 minute | 19 | 0 | 0 | n | y
4170 | Battery Equalize | 1841 | Battery Equalize |  |  | 19 | 0 | 0 | n | y
4173 | Main Battery Disconnect Open | 303 | Battery disconnected |  | 1 minute | 19 | 0 | 0 | n | y
4174 | Battery Temperature Sensor Fault | 332 | Battery temperature fault |  |  | 19 | 0 | 0 | n | y
4175 | Bypass Frequency Error | 513 | Reserve mains frequency outside limits |  | Immediate | 19 | 0 | 0 | n | y
4176 | Battery Circuit Breaker 1 Open | 301 | Battery switch open |  | 1 minute | 19 | 0 | 0 | n | y
4179 | Battery Circuit Breaker 2 Open | 301 | Battery switch open |  | 1 minute | 19 | 0 | 0 | n | y
4182 | Battery Circuit Breaker 3 Open | 301 | Battery switch open | X | 1 minute | 19 | 0 | 0 | n | y
4185 | Battery Circuit Breaker 4 Open | 301 | Battery switch open |  | 1 minute | 19 | 0 | 0 | n | y
4188 | Battery Circuit Breaker 5 Open | 301 | Battery switch open |  | 1 minute | 19 | 0 | 0 | n | y
4191 | Battery Circuit Breaker 6 Open | 301 | Battery switch open |  | 1 minute | 19 | 0 | 0 | n | y
4194 | Battery Circuit Breaker 7 Open | 301 | Battery switch open |  | 1 minute | 19 | 0 | 0 | n | y
4197 | Battery Circuit Breaker 8 Open | 301 | Battery switch open |  | 1 minute | 19 | 0 | 0 | n | y
4200 | Battery Charging Inhibited | 233 | Battery charger inhibit |  |  | 19 | 0 | 0 | n | y
4213 | System Shutdown - EPO | 1111 | Emergency stop operated |  | 10 seconds | 19 | 0 | 0 | n | y
4214 | System Shutdown - REPO | 1864 | System Shutdown - REPO |  | 10 seconds | 19 | 0 | 0 | n | y
4215 | System Output Off | 607 | Output load not supplied | X | Immediate | 19 | 0 | 0 | n | y
4217 | Bypass - Manual Xfr Inhibited | 545 | Transfer to bypass inhibited |  |  | 19 | 0 | 0 | n | y
4218 | Bypass - Manual Rexfr Inhibited | 505 | Reserve inhibited |  | 10 minutes | 19 | 0 | 0 | n | y
4219 | Battery Over Temperature | 315 | High battery temperature |  | 1 minute | 19 | 0 | 0 | n | y
4220 | Battery - External Monitor 1 | 1654 | Battery maintenance recommended |  |  | 19 | 0 | 0 | n | y
4221 | Battery - External Monitor 2 | 1654 | Battery maintenance recommended |  |  | 19 | 0 | 0 | n | y
4222 | Battery Ground Fault | 1832 | Ground Over current |  |  | 19 | 0 | 0 | n | y
4230 | System Output Low Power Factor | 1865 | System Output Low Power Factor |  |  | 19 | 0 | 0 | n | y
4233 | Inverter Failure | 436 | Inverter fault |  | 10 seconds | 19 | 0 | 0 | n | y
4234 | Inverter Overload Phase A | 474 | Inverter overload fault |  | 1 minute | 19 | 0 | 0 | n | y
4235 | Inverter Overload Phase B | 474 | Inverter overload fault |  | 1 minute | 19 | 0 | 0 | n | y
4236 | Inverter Overload Phase C | 474 | Inverter overload fault | X | 1 minute | 19 | 0 | 0 | n | y
4237 | Inverter Inhibit - External | 416 | Inverter inhibited | X | 10 seconds | 19 | 0 | 0 | n | y
4270 | Input Contact 01 | 6 | User input 1 |  |  | 19 | 0 | 0 | n | y
4271 | Input Contact 02 | 7 | User input 2 |  |  | 19 | 0 | 0 | n | y
4272 | Input Contact 03 | 8 | User input 3 |  |  | 19 | 0 | 0 | n | y
4273 | Input Contact 04 | 9 | User input 4 |  |  | 19 | 0 | 0 | n | y
4274 | Input Contact 05 | 10 | User input 5 |  |  | 19 | 0 | 0 | n | y
4275 | Input Contact 06 | 11 | User input 6 |  |  | 19 | 0 | 0 | n | y
4276 | Input Contact 07 | 12 | User input 7 |  |  | 19 | 0 | 0 | n | y
4277 | Input Contact 08 | 13 | User input 8 |  |  | 19 | 0 | 0 | n | y
4278 | Input Contact 09 | 14 | User input 9 |  |  | 19 | 0 | 0 | n | y
4279 | Input Contact 10 | 15 | User input 10 |  |  | 19 | 0 | 0 | n | y
4280 | Input Contact 11 | 16 | User input 11 | X |  | 19 | 0 | 0 | n | y
4281 | Input Contact 12 | 17 | User input 12 | X |  | 19 | 0 | 0 | n | y
4282 | Input Contact 13 | 18 | User input 13 | X |  | 19 | 0 | 0 | n | y
4283 | Input Contact 14 | 1866 | User input 14 |  |  | 19 | 0 | 0 | n | y
4284 | Input Contact 15 | 1867 | User input 15 | SMS |  | 19 | 0 | 0 | y | y
4285 | Input Contact 16 | 1868 | User input 16 | SMS |  | 19 | 0 | 0 | y | y
4286 | Output Amp Over User Limit-Phs A | 1233 | Current limit (phase 1) over threshold 1 alarm | SMS | 10 minutes | 19 | 0 | 0 | y | y
4287 | Output Amp Over User Limit-Phs B | 1235 | Current limit (phase 1) over threshold 2 alarm | SMS | 10 minutes | 19 | 0 | 0 | y | y
4288 | Output Amp Over User Limit-Phs C | 1237 | Current limit (phase 1) over threshold 3 alarm |  | 10 minutes | 19 | 0 | 0 | n | y
4290 | Inverter Shutdown - Overload | 408 | Inhibited due to overload timeout |  | 1 minute | 19 | 0 | 0 | n | y
4294 | Inlet Air Over Temperature | 175 | High input air temperature |  |  | 19 | 0 | 0 | n | y
4295 | Rectifier Failure | 273 | Rectifier fault |  | 10 minutes | 19 | 0 | 0 | n | y
4296 | Rectifier Operation Inhibit-Ext | 208 | Rectifier inhibit |  |  | 19 | 0 | 0 | n | y
4298 | UPS Output on Bypass | 659 | Output load supplied by bypass |  | Immediate | 19 | 0 | 0 | n | y
4299 | Output Load on Maint. Bypass | 606 | Output load supplied through maintenance bypass |  | 1 minute | 19 | 0 | 0 | n | y
4300 | Internal Communications Failure | 71 | Liebert communication fault |  | 1 minute | 19 | 0 | 0 | n | y
4308 | DC Bus Ground Fault - Positive | 323 | Dc earth fault |  |  | 19 | 0 | 0 | n | y
4309 | DC Bus Ground Fault - Negative | 323 | Dc earth fault |  |  | 19 | 0 | 0 | n | y
4310 | Equipment Over Temperature | 419 | Over temperature |  | 1 minute | 19 | 0 | 0 | n | y
4315 | On Generator | 1219 | Generator on load |  |  | 19 | 0 | 0 | n | y
4316 | Auto Restart In Progress | 1869 | Auto Restart In Progress |  |  | 19 | 0 | 0 | n | y
4317 | Auto Restart Inhibited - Ext | 1870 | Auto Restart Inhibited - Ext |  |  | 19 | 0 | 0 | n | y
4323 | Battery Test Failed | 1679 | Battery test failed |  |  | 19 | 0 | 0 | n | y
4325 | Backfeed Breaker Open | 1871 | Backfeed Breaker Open |  |  | 19 | 0 | 0 | n | y
4382 | System Input Current Imbalance | 1845 | System Input Current Imbalance | X | 1 minute | 19 | 0 | 0 | n | y
4383 | Bypass Static Switch Off Extrnl | 543 | Bypass off | X | 1 minute | 19 | 0 | 0 | n | y
4389 | System Output Fault | 642 | Output general fail | X | Immediate | 19 | 0 | 0 | n | y
4390 | Inverter Off - External | 413 | Inverter stopped manually |  | Immediate | 19 | 0 | 0 | n | y
4391 | Inverter Static Switch SCR Short | 445 | Inverter static switch in short circuit |  | 1 minute | 19 | 0 | 0 | n | y
4440 | Fuse Failure | 1600 | One or more fuses blown |  | 1 minute | 19 | 0 | 0 | n | y
4441 | System Controller Error | 71 | Liebert communication fault |  | 1 minute | 19 | 0 | 0 | n | y
4442 | System Breaker(s) Open Failure | 1142 | Mains breaker/contactor fail to open |  | 1 minute | 19 | 0 | 0 | n | y
4726 | Service Required | 108 | Maintenance service recommended |  |  | 19 | 0 | 0 | n | y
4740 | Battery Test Inhibited | 74 | Battery Test not Allowed | X |  | 19 | 0 | 0 | n | y
4741 | Battery Self Test | 280 | Automatic Battery test |  |  | 19 | 0 | 0 | n | y
4742 | Battery Low Shutdown | 326 | End of discharge |  |  | 19 | 0 | 0 | n | y
4747 | Equipment Temperature Sensor Fail | 107 | Output air temperature sensor fault |  | 1 hour | 19 | 0 | 0 | n | y
4749 | System Fan Failure - Redundant | 166 | Fan failure |  |  | 19 | 0 | 0 | n | y
4750 | Multiple Fan Failure | 166 | Fan failure |  |  | 19 | 0 | 0 | n | y
4753 | Main Controller Fault | 1885 | Main controller fault |  | 1 minute | 19 | 0 | 0 | n | y
4754 | System Breaker(s) Close Failure | 1140 | Mains breaker/contactor fail to close |  | 1 minute | 19 | 0 | 0 | n | y
4755 | Input Filter Cycle Lock | 1872 | Input Filter Cycle Lock |  |  | 19 | 0 | 0 | n | y
4823 | Parallel Comm Warning | 1691 | Parallel communication fault | X |  | 19 | 0 | 0 | n | y
4824 | System Comm Fail | 71 | Liebert communication fault |  | 1 minute | 19 | 0 | 0 | n | y
4825 | Loss of Redundancy | 1635 | UPS loss of redundancy |  | 1 minute | 19 | 0 | 0 | n | y
4826 | BPSS Startup Inhibit | 1880 | Parallel Bypass Static Switch Start Inhibited |  |  | 19 | 0 | 0 | n | y
4827 | MMS Transfer Inhibit | 1879 | Parallel BypassTransfer Inhibit |  |  | 19 | 0 | 0 | n | y
4828 | MMS Retransfer Inhibit | 1873 | Parallel Bypass Retransfer Inhibit |  |  | 19 | 0 | 0 | n | y
4830 | MMS Loss of Sync Pulse | 1874 | Parallel Loss of Sync Pulse |  |  | 19 | 0 | 0 | n | y
4831 | MMS Overload | 1689 | Parallel system overload |  | 1 minute | 19 | 0 | 0 | n | y
4834 | MMS On Battery | 1696 | Parallel load on battery |  | 1 minute | 19 | 0 | 0 | n | y
5144 | Output Of/Uf | 641 | Output Frequency outside limits |  | immediate | 19 | 0 | 0 | n | y
5456 | ECO Mode Active | 1875 | ECO Mode Active |  |  | 19 | 0 | 0 | n | y
5561 | LBS Active - Master | 1876 | LBS Active - Master | X |  | 19 | 0 | 0 | n | y
5562 | LBS Active - Slave | 1877 | LBS Active - Slave | X |  | 19 | 0 | 0 | n | y
5768 | Outlet Air Overtemperature Limit | 133 | Temperature too high in device |  | 1 minute | 19 | 0 | 0 | n | y
5769 | EMO Shutdown | 1878 | EMO Shutdown |  | immediate | 19 | 0 | 0 | n | y
4871 | UPS battery1 status | 325 | Battery normal |  |  | 19 | 0 | 0 | n | y
4871 | UPS battery1 status | 306 | Flat battery |  | 1 minute | 19 | 0 | 0 | n | y
4746 | Inverter On/Off State | 448 | Inverter on |  |  | 19 | 0 | 0 | n | y
4746 | Inverter On/Off State | 415 | Inverter off |  | 1 minute | 19 | 0 | 0 | n | y
4299 | Output Load on Maint.Bypass | 627 | Maintenance Bypass switch closed |  | 1 minute | 19 | 0 | 0 | n | y
4123 | System Status | 126 | Ups Warning |  | 1 minute | 19 | 0 | 0 | n | y
4123 | System Status | 1106 | Warning Alarm active |  | 1 minute | 19 | 0 | 0 | n | y
4872 | UPS Output Source | 660 | Output load supplied by inverter |  |  | 19 | 0 | 0 | n | y
4872 | UPS Output Source | 621 | Output load supplied by battery | X | Immediate | 19 | 0 | 0 | n | y
4223 | System Output Pct Power Phase A | 1885 | Main controller fault | X |  | 19 | 0 | 0 | n | y
4224 | System Output Pct Power Phase B | 1885 | Main controller fault | X |  | 19 | 0 | 0 | n | y
4225 | System Output Pct Power Phase C | 1885 | Main controller fault |  |  | 19 | 0 | 0 | n | y
4122 | System Input Power Problem | 202 | Primary mains power failure |  | Immediate | 0 | 0 | 0 | n | y
4132 | Bypass Overload Phase A | 594 | Bypass overload operation |  | 1 minute | 0 | 0 | 0 | n | y
4133 | Bypass Overload Phase B | 594 | Bypass overload operation |  | 1 minute | 0 | 0 | 0 | n | y
4134 | Bypass Overload Phase C | 594 | Bypass overload operation |  | 1 minute | 0 | 0 | 0 | n | y
4135 | Bypass Not Available | 593 | Bypass mains power failure |  | Immediate | 0 | 0 | 0 | n | y
4138 | Bypass Auto Retransfer Failed | 545 | Transfer to bypass inhibited |  |  | 0 | 0 | 0 | n | y
4139 | Bypass - Excess Auto Retransfers | 545 | Transfer to bypass inhibited |  |  | 0 | 0 | 0 | n | y
4142 | Bypass Static Switch Overload | 650 | Static switch overload warning |  | 10 minutes | 0 | 0 | 0 | n | y
4143 | Bypass Static Switch Unavailable | 579 | Bypass static switch fault / meas. defective |  |  | 0 | 0 | 0 | n | y
4144 | Bypass Excessive Pulse Parallel | 1861 | Bypass Excessive Pulse Parallel |  |  | 0 | 0 | 0 | n | y
4145 | Bypass Auto Transfer Failed | 1862 | Bypass Auto Transfer Failed |  |  | 0 | 0 | 0 | n | y
4146 | System Input Phs Rotation Error | 204 | Primary mains wrong phase rotation |  | 1 minute | 0 | 0 | 0 | n | y
4147 | System Input Current Limit | 423 | Current limit |  | 1 minute | 0 | 0 | 0 | n | y
4162 | Battery Low | 309 | Battery Shutdown Imminent |  | 10 minutes | 0 | 0 | 0 | n | y
4164 | Battery Charging Error | 232 | Battery charger failure |  | 10 minutes | 0 | 0 | 0 | n | y
4165 | Battery Charging Reduced-Extrnl | 1863 | Battery Charging Reduced-Extrnl |  |  | 0 | 0 | 0 | n | y
4166 | Battery Capacity Low | 338 | Battery capacity too small | X | 1 minute | 0 | 0 | 0 | n | y
4168 | Battery Discharging | 308 | Battery discharging | X |  | 0 | 0 | 0 | n | y
4169 | Battery Temperature Imbalance | 315 | High battery temperature | X | 1 minute | 0 | 0 | 0 | n | y
4170 | Battery Equalize | 1841 | Battery Equalize |  |  | 0 | 0 | 0 | n | y
4173 | Main Battery Disconnect Open | 303 | Battery disconnected |  | 1 minute | 0 | 0 | 0 | n | y
4174 | Battery Temperature Sensor Fault | 332 | Battery temperature fault |  |  | 0 | 0 | 0 | n | y
4175 | Bypass Frequency Error | 513 | Reserve mains frequency outside limits |  | Immediate | 0 | 0 | 0 | n | y
4176 | Battery Circuit Breaker 1 Open | 301 | Battery switch open |  | 1 minute | 0 | 0 | 0 | n | y
4179 | Battery Circuit Breaker 2 Open | 301 | Battery switch open |  | 1 minute | 0 | 0 | 0 | n | y
4182 | Battery Circuit Breaker 3 Open | 301 | Battery switch open | X | 1 minute | 0 | 0 | 0 | n | y
4185 | Battery Circuit Breaker 4 Open | 301 | Battery switch open |  | 1 minute | 0 | 0 | 0 | n | y
4188 | Battery Circuit Breaker 5 Open | 301 | Battery switch open |  | 1 minute | 0 | 0 | 0 | n | y
4191 | Battery Circuit Breaker 6 Open | 301 | Battery switch open |  | 1 minute | 0 | 0 | 0 | n | y
4194 | Battery Circuit Breaker 7 Open | 301 | Battery switch open |  | 1 minute | 0 | 0 | 0 | n | y
4197 | Battery Circuit Breaker 8 Open | 301 | Battery switch open |  | 1 minute | 0 | 0 | 0 | n | y
4200 | Battery Charging Inhibited | 233 | Battery charger inhibit |  |  | 0 | 0 | 0 | n | y
4213 | System Shutdown - EPO | 1111 | Emergency stop operated |  | 10 seconds | 0 | 0 | 0 | n | y
4214 | System Shutdown - REPO | 1864 | System Shutdown - REPO |  | 10 seconds | 0 | 0 | 0 | n | y
4215 | System Output Off | 607 | Output load not supplied | X | Immediate | 0 | 0 | 0 | n | y
4217 | Bypass - Manual Xfr Inhibited | 545 | Transfer to bypass inhibited |  |  | 0 | 0 | 0 | n | y
4218 | Bypass - Manual Rexfr Inhibited | 505 | Reserve inhibited |  | 10 minutes | 0 | 0 | 0 | n | y
4219 | Battery Over Temperature | 315 | High battery temperature |  | 1 minute | 0 | 0 | 0 | n | y
4220 | Battery - External Monitor 1 | 1654 | Battery maintenance recommended |  |  | 0 | 0 | 0 | n | y
4221 | Battery - External Monitor 2 | 1654 | Battery maintenance recommended |  |  | 0 | 0 | 0 | n | y
4222 | Battery Ground Fault | 1832 | Ground Over current |  |  | 0 | 0 | 0 | n | y
4230 | System Output Low Power Factor | 1865 | System Output Low Power Factor |  |  | 0 | 0 | 0 | n | y
4233 | Inverter Failure | 436 | Inverter fault |  | 10 seconds | 0 | 0 | 0 | n | y
4234 | Inverter Overload Phase A | 474 | Inverter overload fault |  | 1 minute | 0 | 0 | 0 | n | y
4235 | Inverter Overload Phase B | 474 | Inverter overload fault |  | 1 minute | 0 | 0 | 0 | n | y
4236 | Inverter Overload Phase C | 474 | Inverter overload fault | X | 1 minute | 0 | 0 | 0 | n | y
4237 | Inverter Inhibit - External | 416 | Inverter inhibited | X | 10 seconds | 0 | 0 | 0 | n | y
4270 | Input Contact 01 | 6 | User input 1 |  |  | 0 | 0 | 0 | n | y
4271 | Input Contact 02 | 7 | User input 2 |  |  | 0 | 0 | 0 | n | y
4272 | Input Contact 03 | 8 | User input 3 |  |  | 0 | 0 | 0 | n | y
4273 | Input Contact 04 | 9 | User input 4 |  |  | 0 | 0 | 0 | n | y
4274 | Input Contact 05 | 10 | User input 5 |  |  | 0 | 0 | 0 | n | y
4275 | Input Contact 06 | 11 | User input 6 |  |  | 0 | 0 | 0 | n | y
4276 | Input Contact 07 | 12 | User input 7 |  |  | 0 | 0 | 0 | n | y
4277 | Input Contact 08 | 13 | User input 8 |  |  | 0 | 0 | 0 | n | y
4278 | Input Contact 09 | 14 | User input 9 |  |  | 0 | 0 | 0 | n | y
4279 | Input Contact 10 | 15 | User input 10 |  |  | 0 | 0 | 0 | n | y
4280 | Input Contact 11 | 16 | User input 11 | X |  | 0 | 0 | 0 | n | y
4281 | Input Contact 12 | 17 | User input 12 | X |  | 0 | 0 | 0 | n | y
4282 | Input Contact 13 | 18 | User input 13 | X |  | 0 | 0 | 0 | n | y
4283 | Input Contact 14 | 1866 | User input 14 |  |  | 0 | 0 | 0 | n | y
4284 | Input Contact 15 | 1867 | User input 15 | SMS |  | 0 | 0 | 0 | y | y
4285 | Input Contact 16 | 1868 | User input 16 | SMS |  | 0 | 0 | 0 | y | y
4286 | Output Amp Over User Limit-Phs A | 1233 | Current limit (phase 1) over threshold 1 alarm | SMS | 10 minutes | 0 | 0 | 0 | y | y
4287 | Output Amp Over User Limit-Phs B | 1235 | Current limit (phase 1) over threshold 2 alarm | SMS | 10 minutes | 0 | 0 | 0 | y | y
4288 | Output Amp Over User Limit-Phs C | 1237 | Current limit (phase 1) over threshold 3 alarm |  | 10 minutes | 0 | 0 | 0 | n | y
4290 | Inverter Shutdown - Overload | 408 | Inhibited due to overload timeout |  | 1 minute | 0 | 0 | 0 | n | y
4294 | Inlet Air Over Temperature | 175 | High input air temperature |  |  | 0 | 0 | 0 | n | y
4295 | Rectifier Failure | 273 | Rectifier fault |  | 10 minutes | 0 | 0 | 0 | n | y
4296 | Rectifier Operation Inhibit-Ext | 208 | Rectifier inhibit |  |  | 0 | 0 | 0 | n | y
4298 | UPS Output on Bypass | 659 | Output load supplied by bypass |  | Immediate | 0 | 0 | 0 | n | y
4299 | Output Load on Maint. Bypass | 606 | Output load supplied through maintenance bypass |  | 1 minute | 0 | 0 | 0 | n | y
4300 | Internal Communications Failure | 71 | Liebert communication fault |  | 1 minute | 0 | 0 | 0 | n | y
4308 | DC Bus Ground Fault - Positive | 323 | Dc earth fault |  |  | 0 | 0 | 0 | n | y
4309 | DC Bus Ground Fault - Negative | 323 | Dc earth fault |  |  | 0 | 0 | 0 | n | y
4310 | Equipment Over Temperature | 419 | Over temperature |  | 1 minute | 0 | 0 | 0 | n | y
4315 | On Generator | 1219 | Generator on load |  |  | 0 | 0 | 0 | n | y
4316 | Auto Restart In Progress | 1869 | Auto Restart In Progress |  |  | 0 | 0 | 0 | n | y
4317 | Auto Restart Inhibited - Ext | 1870 | Auto Restart Inhibited - Ext |  |  | 0 | 0 | 0 | n | y
4323 | Battery Test Failed | 1679 | Battery test failed |  |  | 0 | 0 | 0 | n | y
4325 | Backfeed Breaker Open | 1871 | Backfeed Breaker Open |  |  | 0 | 0 | 0 | n | y
4382 | System Input Current Imbalance | 1845 | System Input Current Imbalance | X | 1 minute | 0 | 0 | 0 | n | y
4383 | Bypass Static Switch Off Extrnl | 543 | Bypass off | X | 1 minute | 0 | 0 | 0 | n | y
4389 | System Output Fault | 642 | Output general fail | X | Immediate | 0 | 0 | 0 | n | y
4390 | Inverter Off - External | 413 | Inverter stopped manually |  | Immediate | 0 | 0 | 0 | n | y
4391 | Inverter Static Switch SCR Short | 445 | Inverter static switch in short circuit |  | 1 minute | 0 | 0 | 0 | n | y
4440 | Fuse Failure | 1600 | One or more fuses blown |  | 1 minute | 0 | 0 | 0 | n | y
4441 | System Controller Error | 71 | Liebert communication fault |  | 1 minute | 0 | 0 | 0 | n | y
4442 | System Breaker(s) Open Failure | 1142 | Mains breaker/contactor fail to open |  | 1 minute | 0 | 0 | 0 | n | y
4726 | Service Required | 108 | Maintenance service recommended |  |  | 0 | 0 | 0 | n | y
4740 | Battery Test Inhibited | 74 | Battery Test not Allowed | X |  | 0 | 0 | 0 | n | y
4741 | Battery Self Test | 280 | Automatic Battery test |  |  | 0 | 0 | 0 | n | y
4742 | Battery Low Shutdown | 326 | End of discharge |  |  | 0 | 0 | 0 | n | y
4747 | Equipment Temperature Sensor Fail | 107 | Output air temperature sensor fault |  | 1 hour | 0 | 0 | 0 | n | y
4749 | System Fan Failure - Redundant | 166 | Fan failure |  |  | 0 | 0 | 0 | n | y
4750 | Multiple Fan Failure | 166 | Fan failure |  |  | 0 | 0 | 0 | n | y
4753 | Main Controller Fault | 1885 | Main controller fault |  | 1 minute | 0 | 0 | 0 | n | y
4754 | System Breaker(s) Close Failure | 1140 | Mains breaker/contactor fail to close |  | 1 minute | 0 | 0 | 0 | n | y
4755 | Input Filter Cycle Lock | 1872 | Input Filter Cycle Lock |  |  | 0 | 0 | 0 | n | y
4823 | Parallel Comm Warning | 1691 | Parallel communication fault | X |  | 0 | 0 | 0 | n | y
4824 | System Comm Fail | 71 | Liebert communication fault |  | 1 minute | 0 | 0 | 0 | n | y
4825 | Loss of Redundancy | 1635 | UPS loss of redundancy |  | 1 minute | 0 | 0 | 0 | n | y
4826 | BPSS Startup Inhibit | 1880 | Parallel Bypass Static Switch Start Inhibited |  |  | 0 | 0 | 0 | n | y
4827 | MMS Transfer Inhibit | 1879 | Parallel BypassTransfer Inhibit |  |  | 0 | 0 | 0 | n | y
4828 | MMS Retransfer Inhibit | 1873 | Parallel Bypass Retransfer Inhibit |  |  | 0 | 0 | 0 | n | y
4830 | MMS Loss of Sync Pulse | 1874 | Parallel Loss of Sync Pulse |  |  | 0 | 0 | 0 | n | y
4831 | MMS Overload | 1689 | Parallel system overload |  | 1 minute | 0 | 0 | 0 | n | y
4834 | MMS On Battery | 1696 | Parallel load on battery |  | 1 minute | 0 | 0 | 0 | n | y
5144 | Output Of/Uf | 641 | Output Frequency outside limits |  | immediate | 0 | 0 | 0 | n | y
5456 | ECO Mode Active | 1875 | ECO Mode Active |  |  | 0 | 0 | 0 | n | y
5561 | LBS Active - Master | 1876 | LBS Active - Master | X |  | 0 | 0 | 0 | n | y
5562 | LBS Active - Slave | 1877 | LBS Active - Slave | X |  | 0 | 0 | 0 | n | y
5768 | Outlet Air Overtemperature Limit | 133 | Temperature too high in device |  | 1 minute | 0 | 0 | 0 | n | y
5769 | EMO Shutdown | 1878 | EMO Shutdown |  | immediate | 0 | 0 | 0 | n | y
4871 | UPS battery1 status | 325 | Battery normal |  |  | 0 | 0 | 0 | n | y
4871 | UPS battery1 status | 306 | Flat battery |  | 1 minute | 0 | 0 | 0 | n | y
4746 | Inverter On/Off State | 448 | Inverter on |  |  | 0 | 0 | 0 | n | y
4746 | Inverter On/Off State | 415 | Inverter off |  | 1 minute | 0 | 0 | 0 | n | y
4299 | Output Load on Maint.Bypass | 627 | Maintenance Bypass switch closed |  | 1 minute | 0 | 0 | 0 | n | y
4123 | System Status | 126 | Ups Warning |  | 1 minute | 0 | 0 | 0 | n | y
4123 | System Status | 1106 | Warning Alarm active |  | 1 minute | 0 | 0 | 0 | n | y
4872 | UPS Output Source | 660 | Output load supplied by inverter |  |  | 0 | 0 | 0 | n | y
4872 | UPS Output Source | 621 | Output load supplied by battery | X | Immediate | 0 | 0 | 0 | n | y
4223 | System Output Pct Power Phase A | 1885 | Main controller fault | X |  | 0 | 0 | 0 | n | y
4224 | System Output Pct Power Phase B | 1885 | Main controller fault | X |  | 0 | 0 | 0 | n | y
4225 | System Output Pct Power Phase C | 1885 | Main controller fault |  |  | 0 | 0 | 0 | n | y
Note on B1: IP Address for the Velocity Simulator. Use 127.0.0.1 if this script is running on same PC as Simulator. -or- Use address of remote PC where the simulator is running. Ensure that "Remote Control" check box is enabled on the Velocity simulator
Note on C1: Email address
Note on F1: 10.16.67.249 = inetmail.emersn.net
Note on G1: Send email when test is complete if enable = y (Yes)
Note on F2: Delay until 'call' is made to the LIFE Station after Active Event transition. If cell is empty, the event is sent with the next Routine call
Note on G2: Clear = 0 Message = 3 Warn = 11 Alarm = 19 Fault = 27
Note on H2: Commonly indexed points are: Battery Cabinets on UPS systems. Temp semsors of Cooling systems. Where: 0 is the first, 1 is the second, etc.
Note on I2: The delay starts after the Event State transition. This delay is combined with EmerDelay when it is enabled (y). If EmerDelay is set to "n" then only this delay will be used.
Note on J2: Use Emergency Delay: y = Yes n = No Emergency Delay is added to the Optional Delay Example 1: EmerDelay = 1 minute Opt Delay = 10 sec Cell in this Column = y Step delay = 70 seconds. Example 2: EmerDelay = 1 minute Opt Delay = 10 sec Cell in this Column = n Step delay = 10 seconds.
Note on K2: Run this step: y = Yes n = No use lower case

## Reference
PointId | LifeId | life event | ORed event | EmerCall | EmerDelay | InReport | Emergency Call Status | Other Call Status | Alarm Condition | PgmName | Point Label | EngReference | EngDescription
| 0 | Events Data lost |  | No |  | No | Normal | Normal | event
| 1 | Service active |  | Yes | 18 hours | Yes | Warning | Warning | event
| 2 | Adjust time |  | No |  | No | Normal | Normal | event
| 990 | Negative Adjust time |  | No |  | No | Normal | Normal | event
| 1659 | UPS board hasn't detected the UPS |  | Yes | 1 hour | No | Severe Warning | Severe Warning | event
| 1860 | Changed SN or type |  | Yes | Immediate | No | Alarm | Alarm | event
| 5 | Unit just supplied |  | Yes | Immediate | No | Severe Warning | Warning | event
| 84 | Measures Data lost |  | No |  | No | Normal | Normal | event
4122 | 202 | Primary mains power failure |  | Yes | Immediate | Yes | Normal | Normal | event | evt_sys_inpNotQualified | System Input Power Problem | Mains Volt. Abnormal, Mains freq.abnormal | The input is not qualified to provide power to the system. This may be due to system input over-voltage, system input under-voltage, system input frequency out of range, or other similar issues.This data definition is intended to be used with devices that only have one system input. The system input may be single, 2-phase or 3-phase. A system bypass input is NOT considered to be a second system input. For system bypass input definitions see @todo.Do NOT use this data definition if the device has more that one system input. An example of a device that has more than one system input is the STS2. For devices with multiple system inputs, see the following data definitions: @todo.The system input is defined as the source of power (utility or mains) for the device.
4135 | 593 | Bypass mains power failure |  | Yes | Immediate | Yes | Normal | Normal | event | evt_byp_unavail | Bypass Not Available | Bypass Fault , Bypass phase reverse, Bypass over current | This summary event is asserted when the bypass is not available. Possible reasons for this might include, but are not limited to the following: Bypass Sync Error, Bypass Line Fail, Bypass Overvoltage, Bypass Undervoltage, Bypass Phase Rotation Error, etc.
4139 | 545 | Transfer to bypass inhibited |  | No |  | No | Normal | Normal | event | evt_byp_excessAutoReXfr | Bypass - Excess Auto Retransfers | Transfer time-out | Indicates too many transfers from bypass to inverter have occurred in the specified time interval. Automatic retransfer to inverter is inhibited (manual retransfer may still be allowed).
4143 | 579 | Bypass static switch fault / meas. defective |  | No |  | No | Normal | Normal | event | evt_byp_sbsUnavail | Bypass Static Switch Unavailable | Bypass STS fail | Summary event based on the detection of a SBS failure. Some of the possible causes include, but are not limited to the following: SBS Phase Open , SBS SCR Shorted, Static Bypass Switch Overload Exceeded, Bypass Power Supply Fail, Static Bypass Switch Fuse Failure, etc
4146 | 204 | Primary mains wrong phase rotation |  | Yes | 1 minute | Yes | Alarm | Warning | event | evt_sys_inpPhsRotation | System Input Phs Rotation Error | Mains phase reversed | The power conductors on the input line are not wired to the UPS in the sequence preferred for the rectifier (A-B-C).With the input source voltage above minimum threshold, the phase rotation is not A-B-C.It becomes inactive when the phase rotation is A-B-C with source voltage above minimum threshold.
4162 | 309 | Battery Shutdown Imminent |  | Yes | 10 minutes | Yes | Severe Warning | Severe Warning | event | evt_bat_low | Battery Low | Battery low pre-warning | The calculated battery time remaining has reached the battery low threshold. This event is NOT active during a battery test or while operating on mains/utility.It becomes inactive when the calculated battery time remaining is above the low battery threshold, or normal operation on utility/mains resumes. This event may or may not remain active past the end-of-discharge.
4164 | 232 | Battery charger failure |  | Yes | 10 minutes | No | Severe Warning | Warning | event | evt_bat_chargeError | Battery Charging Error |  | The battery is not charging properly. This could be caused by a number of reasons, including but not limited to: battery charger failure, battery failure, etc.It becomes inactive when battery charging returns to normal.
4166 | 338 | Battery capacity too small |  | Yes | 1 minute | No | Normal | Normal | event | evt_bat_capacityLow | Battery Capacity Low |  | The battery capacity is low. There are various possible reasons for this event, including but not limited to: a battery is offline, the battery age has reduced its capabilities, etc.It becomes inactive when normal battery capacity is restored.For a system configuration without batteries, this event should not be supported.
4168 | 308 | Battery discharging |  | No |  | Yes | Normal | Normal | event | evt_bat_discharging | Battery Discharging |  | The battery is discharging. This is active when power is being withdrawn from the battery. NOTE: This is not activated due to a battery test.It becomes inactive when the batteries are charging.
4170 | 1841 | Battery Equalize |  | No |  | No | Normal | Normal | event | evt_bat_equalize | Battery Equalize |  | The rectifier output voltage is increased to equalize the battery voltage level.It becomes inactive when the equalize algorithm completes OR battery discharge is required.
4172 | 312 | Battery test |  | No |  | Yes | Normal | Normal | event | evt_bat_autoTest | Battery Auto Test In Progress |  | Automatic battery test is in progress. A battery test is in process and will continue until the test completes or terminates due to an external event.It becomes inactive when the test completes or terminates due to an external event.See 'evt_bat_manualTest'
4173 | 303 | Battery disconnected |  | Yes | 1 minute | Yes | Severe Warning | Severe Warning | event | evt_bat_mainDisconnectOpen | Main Battery Disconnect Open |  | Main battery disconnect is open.It becomes inactive when the main battery disconnect is closed.
4200 | 233 | Battery charger inhibit |  | No |  | No | Normal | Normal | event | evt_bat_chargeInhibit | Battery Charging Inhibited |  | Battery charging is inhibited due to an external inhibit signal.It becomes inactive when the external inhibit signal clears, thus allowing normal battery charging.
4213 | 1111 | Emergency stop operated |  | Yes | 10 seconds | No | Severe Warning | Warning | event | evt_sys_outEPO | System Shutdown - EPO | EPO | System shutdown due to Emergency Power Off (EPO) or Emergency Module Off (EMO).
4219 | 315 | High battery temperature |  | Yes | 1 minute | Yes | Severe Warning | Severe Warning | event | evt_bat_tempOver | Battery Over Temperature | battery overtemp of group 1 overtemp | A battery temperature is above a threshold.It becomes inactive when the battery temperature is below the activation threshold or below a specified percentage of the threshold.
4233 | 436 | Inverter fault |  | Yes | 10 seconds | Yes | Alarm | Warning | event | evt_inv_failure | Inverter Failure | Inverter fault | Inverter failure - inverter output is off.This summary event is based on the detection of at least one inverter fault, which may include but is not limited to: inverter overvoltage, inverter undervoltage, inverter phase A fault, inverter phase B fault, inverter phase C fault, inverter DC fuse fail and inverter output fuse fail.It becomes inactive when all applicable inverter faults clear.
4234 | 474 | Inverter overload fault | X | Yes | 1 minute | Yes | Normal | Normal | event | evt_inv_overloadPhsA | Inverter Overload Phase A | Unit over load | Inverter is operating with an overload on phase A.Phase A of the inverter power limit (power draw and/or amperage draw) has been exceeded.It becomes inactive when phase A of the inverter is no longer overloaded.
4235 | 474 | Inverter overload fault | X | Yes | 1 minute | Yes | Normal | Normal | event | evt_inv_overloadPhsB | Inverter Overload Phase B | Unit over load | Inverter is operating with an overload on phase B.Phase B of the inverter power limit (power draw and/or amperage draw) has been exceeded.It becomes inactive when phase B of the inverter is no longer overloaded.
4236 | 474 | Inverter overload fault | X | Yes | 1 minute | Yes | Normal | Normal | event | evt_inv_overloadPhsC | Inverter Overload Phase C | Unit over load | Inverter is operating with an overload on phase C.Phase C of the inverter power limit (power draw and/or amperage draw) has been exceeded.It becomes inactive when phase C of the inverter is no longer overloaded.
4290 | 408 | Inhibited due to overload timeout |  | Yes | 1 minute | Yes | Alarm | Severe Warning | event | evt_inv_shutdownOverload | Inverter Shutdown - Overload | unit over load timeout | The inverter has shutdown due to a sustained overload.This event does not indicate if the load has been dropped or if the load has been transfered to bypass.At least one phase of the inverter power dissipation limit has been exceeded (Power or RMS current vs time curve). Generally, the UPS will take action to protect the inverter from the overload condition.It becomes inactive when transfer to inverter is permitted or if system is restarted.
4295 | 273 | Rectifier fault |  | Yes | 10 minutes | Yes | Alarm | Warning | event | evt_rct_failure | Rectifier Failure | Rectifier fault, Rectifier overcurrent, soft start fail | Rectifier failure - rectifier is off.Summary event based on the detection of one or more rectifier faults. The possible faults include, but are not limited to the following: Battery Overcharge, DC Overvoltage Steady State, DC Overvoltage Transient, DC Undervoltage Steady State, Rectifier Delta/Wye Current Imbalance, Delta Rectifier Fuse Fail, Wye Rectifier Fuse Fail, Rectifier Sync Loss, Input Current Imbalance, Input Filter Fuse Failure, etc.It becomes inactive when all rectifier faults have cleared.
4298 | 659 | Output load supplied by bypass |  | Yes | Immediate | Yes | Warning | Warning | event | evt_sys_loadOnBypass | UPS Output on Bypass |  | The output power is supplied by the bypass.It becomes inactive when not on bypass.NOTE: It is highly recommended that support for 'st_sys_outputSource' or 'st_load_source' be included if this event is supported.
4299 | 606 | Output load supplied through maintenance bypass |  | Yes | 1 minute | No | Normal | Normal | event | evt_sys_loadOnMaintBypass | Output Load on Maint. Bypass |  | The output power is supplied by the maintenance bypass.It becomes inactive when not on maintenance bypass.NOTE: It is highly recommended that support for 'st_sys_outputSource' or 'st_load_source' be included if this event is supported.
4300 | 71 | Liebert communication fault |  | Yes | 1 minute | No | Normal | Normal | event | evt_sys_internalCommFailure | Internal Communications Failure | inverter comm. fail | The control has detected a communication failure of a component on the internal communication bus. Summary event that indicates that there is an internal communication failure.It becomes inactive when all internal communication problems clear.
4310 | 419 | Over temperature |  | Yes | 1 minute | Yes | Warning | Warning | event | evt_sys_overTemperature | Equipment Over Temperature | Ambient overtemp, rectifier over temp,inv.inductor overtemp,inverter overtemp | Equipment over temperature.Summary event based on the detection of at least one temperature exeeding a threshold. The temperatures may include but are not limited to the following:Outlet Air Over Temperature,Rectifier Heatsink Over Temperature,Inverter Heatsink Over Temperature,Static Bypass Switch Heatsink Over Temperature,SSS Heatsink Over TemperatureBecomes inactive when all temperatures return to normal operating range.
4311 | 166 | Fan failure | X | No |  | No | Warning | Warning | event | evt_sys_fanFailure | System Fan Failure |  | System fan failure - one or more fans have failed.NOTE: This is a failure of one or more fans that are cooling the system internal components, as opposed to an environmental unit's blower failure.Becomes inactive when all fan failures are corrected.
4315 | 1219 | Generator on load |  | No |  | Yes | Normal | Normal | event | evt_sys_inpOnGenerator | On Generator |  | A generator is supplying the power to the system.Becomes inactive when the generator is not supplying the system power.Also see 'st_sys_inpSource'.
4382 | 1845 | System Input Current Imbalance |  | Yes | 1 minute | No | Normal | Normal | event | evt_sys_inpCurrentImbal | System Input Current Imbalance | See 'Raptor_ERS_Events.doc', Event ID 8 input current abnormal | System Input Currents are Imbalanced. The input currents are imbalanced and have reached the level to indicate a failure in the input circuit.Becomes inactive when the difference between any single input phase current and relative to the other input phase currents has returned to normal.RAPTOR SPECIFIC: It is expected that service is required to resolve the current imbalance failure.
4389 | 642 | Output general fail |  | Yes | Immediate | Yes | Alarm | Severe Warning | event | evt_sys_outFault | System Output Fault | See 'Raptor_ERS_Events.doc', Event ID 62 output over voltage | Summary event based on the detection of one or more output faults. An output fault includes, but is not limited to: Output Overvoltage, Output Undervoltage, Output Over/Under Frequency, etc.Becomes inactive when all causal faults clear.
4391 | 445 | Inverter static switch in short circuit |  | Yes | 1 minute | No | Normal | Normal | event | evt_inv_ssSCRShort | Inverter Static Switch SCR Short | See 'Raptor_ERS_Events.doc', Event ID 314 | The system has detected a short across one or more inverter static switch Silicon Controlled Rectifiers. Once asserted, the system requires service to clear the event.
4440 | 1600 | One or more fuses blown |  | Yes | 1 minute | No | Normal | Normal | event | evt_sys_fuseFailure | Fuse Failure | output fuse fail | A summary event indicating one or more fuse failures. This is set when a fuse failure occurs, which may include but not limited to: rectifier fuse, input filter fuse, output fuse, inverter fuse, output filter fuse, bypass fuse, etc. Becomes inactive when all causal faults have cleared.
4758 | 1843 | LBS Inhibited |  | Yes | 1 minute | No | Normal | Normal | event | evt_sys_lbsInhibit | LBS Inhibited | tag=nxlEvents:EventID309 LBS Anormal | With the Load Bus Sync Operation enabled, LBS Voltage RMS is not qualified or LBS Voltage frequency is out of tolerance or LBS Voltage has incorrect phase rotation.Becomes inactive when the Load Bus Sync Operation is disabled or all conditions are cleared.
4823 | 1691 | Parallel communication fault |  | No |  | No | Severe Warning | Severe Warning | event | evt_mms_parCommWarn | Parallel Comm Warning | tag=nxlEvents:EventID320 paraller comm. fail | One of the paralleling control communication busses is no longer communicating within the system. This event recovers when all of the communications busses are communicating. If only the faulty module installed the rectifier will be shut down and the inverter DSP will make the system transfer from inverter side to bypass side if the bypass is qualified. Otherwise, system shutdown will occur. If other modules are installed and operating they will continue supporting load on inverter and DSP will shut down faulty power module and open its output relay. Recovery: Manual recovery is required. Otherwise, enter "maintenance mode". Check every module parallel cable. If the connection is right and tight, it should be considered to replace the PFC MOSFETs, their drive board A1 and/or U1 board if necessary.In addition, the battery converter fault may be set by the rectifier DSP if the input neutral wire is lost. So the input neutral wire should be checked."
4825 | 1635 | UPS loss of redundancy |  | Yes | 1 minute | No | Severe Warning | Severe Warning | event | evt_mms_lossRedundancy | Loss of Redundancy | tag=nxlEvents:EventID330 | The multi-module system has been programmed as a redundant, but has an insufficient number of modules to provide the redundancy. (event 330)
4831 | 611 | Overload | X | Yes | Immediate | No | Alarm | Warning | event | evt_mms_systemOverload | MMS Overload | tag=raptorERS:event140 system over load | Multi-Module System Overload. One or more modules in a multi-module system is reporting an overload on at least one phase. Cleared when the overload condition is removed from all modules.
5149 | 1846 | Battery Not Qualified |  | No |  | No | Severe Warning | Severe Warning | event | evt_bat_notQualified | Battery Not Qualified |  | The UPS battery voltage is not qualified. This event will be detected even in the absence of battery disconnect or when battery disconnecit is open. This event will also become active when the main battery disconnect is open.NXr Specific - The rectifier DSP determines the no battery alarm by detecting any of the following conditions:1.The positive or negative battery voltage RMS is less than 100V, when charger is on. This condition causes no battery" warning immediately.2.The positive or negative battery voltage RMS is less than 100V and more than -60V when charger is off. This condition causes "no battery" warning immediately.3.The positive or negative battery voltage is less than 60V and more than -60V for 2ms.Action:The rectifier DSP will shut down battery charger and discharger on faulty module. And all power modules connected to the same battery can detect this alarm.Recovery:For the first two conditions, the alarm will be cleared automatically 10s after the signal of no battery disappears. For the third condition, the alarm will disappear automatically 1s after the signal of no battery disappears. Otherwise, "maintenance mode" is required. Check the relevant wires of battery and connect the battery again. If the battery is correctly connected, then check the relevant cables connecting from M2 board to U1 DSP board. Else replace the M2 and/or U1 board if necessary." For the 1st condition: once the fault is determined, the rectifier will be locked in battery mode. For the 2nd condition: the faulty module will turn off rectifier and can't work in battery mode. As a result, the inverter can't start either in the faulty module.Recovery: Manual recovery is required. Otherwise, enter "maintenance mode" and check the input neutral wire."
5150 | 382 | Battery reverse connected |  | Yes | 1 minute | No | Normal | Normal | event | evt_bat_reverse | Battery Terminals Reversed |  | The measured battery voltage is a negative value due to reversed battery terminal connections.NXr Specific:Valid for:ImmediatelyCondition:The positive or negative battery voltage is less than -60V.Action req'd:The rectifier DSP will shut down battery charger and discharger on faulty module. And all power modules connected to the same battery can detect this alarm.Recovery:The alarm will be cleared automatically after 10s when the battery voltage larger than -60V. Otherwise, maintenance mode" is required. Check the relevant wires of battery and connect the battery again. If the battery is correctly connected, then check the relevant cables connecting from M2 board to U1 board. Else replace the M2 and/or U1 board if necessary."
5151 | 1683 | Battery converter fail |  | Yes | 1 minute | No | Severe Warning | Severe Warning | event | evt_bat_converterFail | Battery Converter Failure |  | Battery converter failure. The power sub-module rectifier will shutdown. If other power sub-module inverters are available, the UPS module will continue supporting the load. If not enough inverters are available, the multi-module system will transfer to bypass if bypass is available.This is a summary event caused by one or more power sub-modules in a UPS module.NXr Specific:Valid for:Depend on conditions.Condition:The rectifier DSP determines the battery converter fault by detecting any of the following conditions when the rectifier is working in the battery mode (we call it discharger below):- DC bus voltage of positive or negative side is more than 486V in hardware. This sets batt. converter fault" for 20ms.- DC bus voltage of positive or negative side is more than 450V for 8.4s when discharger is on.- DC bus voltage of positive or negative side is less than 260V for 400ms when discharger is on and finishes the soft start stage.Action req'd:
5152 | 617 | Inverter static switch open |  | Yes | 1 minute | Yes | Warning | Warning | event | evt_inv_ssSCROpen | Inverter SCR Open |  | The system has detected an Open across one or more inverter static switch Silicon Controlled Rectifiers. Once asserted, the system requires service to clear the event.NXr Specific - Also see evt_inv_ssSCRShort since the specific description discusses both Open and Short conditions.Valid for: Depend on conditionsCondition: The inverter DSP determines the inverter SCR failure by detecting any of the following conditions:-At least one phase output voltage RMS is more than 120V for 1s. Maintenance bypass switch is open and without bypass SCR's drive signal and inverter output relay's drive signal. Especially for parallel system, system must be in the bypass side and without bypass SCR's drive signal in the bus. If the inverter isn't off, these conditions will cause the inverter relay short circuit fault.-When the inverter is off, any one phase output voltage RMS is more than 120V. The local inverter relay is open. The difference between output voltage and inverter voltage is less than 20V. The inverter current RMS is more than 4.4% of nominal current. All these conditions valid for 500ms will cause the inverter relay short circuit fail.- When inverter is off, but at least one phase inverter voltage RMS is more than 120V for 10 minutes. This condition will set inverter relay short circuit fault.- The difference of inverter voltage RMS and output voltage RMS is out of 15% nominal output voltage with inverter relay's drive valid for 5s. This sets inverter relay open circuit fault.- The difference of inverter voltage and output voltage is more than 54V with inverter relay's drive valid for 5.25ms (or more than 108V with inverter relay's drive valid for 2.625ms, or more than 162V with inverter relay's drive valid for 1.3125ms). This sets inverter relay open circuit fault.- Any one phase apparent power is less than 10% of nominal power and the average apparent power of this phase is more than 30% of nominal power with inverter relay's drive valid for 400ms. This condition will set inverter relay open circuit fault.Action req'd: If the inverter relay is short circuit, the inverter DSP will shut down the faulty power module and open the output relay, remaining power modules will continue to maintain load on inverter. If only the faulty module available the power module will shutdown and the system will transfer from inverter side to bypass side if bypass is qualified. Otherwise, system shutdown will occur. The fault is locked until faulty module is power off. If the inverter relay is open circuit, the faulty module will turn off the inverter if bypass is qualified or the number of modules which are working in the inverter side is more than 1 in the system. Otherwise, the inverter works continuously. The fault is locked until faulty module is power off.Recovery: Maintenance mode" is required. Check that the inverter relay is open circuit or short circuit, also check the drive circuit. Replace them if necessary. If the inverter relay is ok, then check the relevant wires from U1 board to M2 board. Else replace the M2, and/or U1 board if necessary."
5153 | 1847 | Load Sharing Fault |  | No |  | No | Warning | Warning | event | evt_load_sharingFault | Load Sharing Fault |  | Difference between any phase inverter current of unit and the relevant average output current of parallel system is more than a specific % of nominal current.NXr Specific:Valid for: 1.25sCondition: Difference between any phase inverter current of unit and the relevant average output current of parallel system is more than 30% of nominal current.Action req'd: None.Recovery: The alarm will be cleared after 1.25s if the differences of three phases' current are less than 30% of nominal current. Otherwise, maintenance mode" is required. Verify the power connection of output in parallel system. Verify the connection status of module parallel cables. Verify the waveform or stability of output voltage. Check the relevant wires from M2 board to U1 control board. Else replace the X3 and/or M2 and/or U1 board if necessary."
5154 | 1848 | DC Bus Abnormal |  | Yes | 1 minute | No | Severe Warning | Severe Warning | event | evt_dcb_ep_abnormal | DC Bus Abnormal |  | The system has detected an abnormal DC Bus Voltage.NXr Specific -DC BUS ABNORMALValid for: Depend on conditionsCondition: The inverter DSP determines the DC bus abnormal fault by detecting any of the following conditions when inverter is on:- Sum of positive DC bus voltage and negative DC bus voltage is less than 560V, valid for immediacy.- Sum of positive DC bus voltage and negative DC bus voltage is less than 620V for 10s.- Either positive DC bus voltage or negative DC bus voltage is more than 486V in hardware for 3ms when inverter is on.- Rectifier is off when inverter is on.Action req'd: The inverter DSP on faulty module will take the power module off line and remaining power modules will maintain load on inverter. If only faulty module available system will transfer from inverter side to bypass side if bypass is qualified. Otherwise, system shutdown will occur.Recovery: If the inverter transfers from bypass side to inverter side automatically after dc bus recoveries normal, then check that the user has added large load to the UPS. Suggest user avoid applying large impact load abruptly. Otherwise, then enter maintenance mode", check if there are relevant faults in rectifier side such as "Rectifier fault", if not, check BUS_+ BUS_- and BUS_N. If there is short circuit, repair it. Otherwise, check the relevant signals from M2 board to U1 control board. Else replace the M2 and/or U1 board if necessary.DC BUS OVER VOLTAGEValid for:
5155 | 1668 | main neutral lost |  | Yes | 1 minute | Yes | Severe Warning | Severe Warning | event | evt_sys_inpNeutralLost | Mains Input Neutral Lost |  | Loss of neutral in the input source is detected.NXr Specific:Valid for: Depend on conditions.Condition: The rectifier DSP determines this fault by detecting any of the following conditions when the rectifier is working in the mains input mode:1. All the DC component of the three-phase mains input voltage is more than 20V for 20~64ms when rectifier finish soft start and output relay is closed. The rectifier will transfer to battery mode and return to mains input mode after 5s for the first time. If the condition is fulfilled again in the next 1.5min, mains neutral lost" will be set.2. The DC component of input voltage is more than 20V for 400ms while rectifier is in soft start stage.Action req'd:
5156 | 1849 | Load Impact Transfer |  | No |  | No | Warning | Warning | event | evt_sys_loadImpactTransfer | Load Impact Transfer |  | On bypass as result of load impact.NXr Specific-Valid for: About 7msCondition: The inverter DSP determines the load impact transfer if the inverter output voltage is less than 60% nominal inverter voltage for 7ms, and bypass is in the sync. range, and system is locked, and the deviation of bypass voltage RMS of three phases from output nominal voltage does not exceed 8%, and without bypass SCR open fault.Action req'd: The faulty module will transfer from inverter side to bypass side and send signal to other modules to make them transfer to bypass side.Recovery: The system will retransfer to inverter side automatically if the load is less than 95% load capacity of inverter-on modules. Suggest user avoid applying large impact load abruptly or short circuit.
5157 | 1850 | User Operation Invalid |  | No |  | Yes | Warning | Warning | event | evt_sys_userOperationInvalid | User Operation Invalid |  | User attempted an invalid operation. This is a notification event.Example: User closed the maintenance bypass switch while module is on inverter.
5158 | 1851 | Power Sub Module Fault |  | No |  | No | Warning | Warning | event | evt_power_sub_module_fault | Power Sub Module Fault |  | Inverter DSP or Rectifier DSP detect one fault in the power sub module.
5770 | 166 | Fan failure | X | No |  | No | Warning | Warning | event | evt_sys_TopOutletFanFault | Top Outlet Fan Fault |  | Top outlet fan fault - one or more top outlet fans have failed.NOTE: This is a failure of one or more fans that are cooling the system internal components, as opposed to an environmental unit's blower failure.Becomes inactive when all fan failures are corrected.
5771 | 611 | Overload | X | Yes | Immediate | No | Alarm | Warning | event | evt_mms_apOverLimit | MMS Over Capacity |  | Multi-Module System over capacity, the load is larger than the unit setting apparent power. Cleared when the load is smaller than the unit setting KVA.APM/NXR Specific: The multi-module system load is larger than the unit setting KVA by paramset.
4872 | 607 | Output load not supplied |  | Yes | Immediate | Yes | Alarm | Severe Warning | =2 | st_sys_upsOutputSource | UPS Output Source
4871 | 325 | Battery normal |  | No |  | No | Normal | Normal | =2 | st_bat_upsBattStatus | UPS battery1 status
4871 | 306 | Flat battery |  | Yes | 1 minute | No | Severe Warning | Severe Warning | =4 | st_bat_upsBattStatus | UPS battery1 status
4746 | 448 | Inverter on |  | No |  | Yes | Normal | Normal | =1 | st_inv_opState | Inverter On/Off State
4746 | 415 | Inverter off |  | Yes | 1 minute | Yes | Alarm | Warning | 0 | st_inv_opState | Inverter On/Off State
4299 | 627 | Maintenance Bypass switch closed |  | Yes | 1 minute | Yes | Alarm | Warning | event | evt_sys_loadOnMaintBypass | Output Load on Maint.Bypass
4123 | 126 | Ups Warning |  | Yes | 1 minute | No | Warning | Warning | 8 | st_sys_status | System Status
4123 | 1106 | Warning Alarm active |  | Yes | 1 minute | No | Warning | Warning | 16 | st_sys_status | System Status
4872 | 660 | Output load supplied by inverter |  | No |  | Yes | Normal | Normal | =3 | st_sys_upsOutputSource | UPS Output Source
4872 | 621 | Output load supplied by battery |  | Yes | Immediate | Yes | Warning | Warning | =5 | st_sys_upsOutputSource | UPS Output Source
4223 | 1885 | Main controller fault | X | No |  | Yes | Warning | Warning | >85 | val_sys_pct_outPwrPhsAN | System Output Pct Power Phase A
4224 | 1885 | Main controller fault | X | No |  | Yes | Warning | Warning | >85 | val_sys_pct_outPwrPhsBN | System Output Pct Power Phase B
4225 | 1885 | Main controller fault | X | No |  | Yes | Warning | Warning | >85 | val_sys_pct_outPwrPhsCN | System Output Pct Power Phase C
4156 | 316 | Battery temperature out of range |  | Yes | 1 minute | Yes | Alarm | Severe Warning | 0 >= val <=40 | val_bat_temp_cabinet | Battery Temperature for Cabinet
| 647 | Load on bypass warning | SMS | Yes | Immediate | No | Alarm | Warning | same as ev 659 datapoint 4298
| 270 | Emergency primary mains failure | SMS | Yes | Immediate | No | Alarm | Warning | same as ev 202 datapoint 4122
| 243 | Primary Mains power recovered | SMS | Yes | Immediate | No | Alarm | Warning | recover from ev 270
| 572 | Emergency reserve supply failure | SMS | Yes | Immediate | No | Alarm | Warning | same as ev 593 datapoint 4135